## technologies and projects
financial base year
2016
| Data from HSIS Appendix A, http://www.hnei.hawaii.edu/sites/www.hnei.hawaii.edu/files/Hawaii%20Solar%20Integration%20Study%20-%20Oahu.pdf | [7 empty] | min->2 | 2->3 | 3->4 | 4->max
[5 empty] | Power Points (MW) |  |  |  |  | Incremental Heat Rate (Btu/kWh) |  |  |  |  | Variable Cost |  | Outages | Fuel Consumption (MMBTU/hour)
[5 empty] | PP | PP | PP | PP | PP | IHR | IHR | IHR | IHR |  |  |  |  | FC | FC | FC | FC | FC
| technology | Plant | Fuel | Fuel Input @ Min Power (MMBtu) | Min | 2 | 3 | 4 | Max | 1 | 2 | 3 | 4 | Full Load Heat Rate (Btu/kWh) | Variable O&M ($/mwH) | Variable Cost ($/Hour) | FOR % | Min | 2 | 3 | 4 | Max | Full load heat rate (calculated) | Err
| Honolulu_8 | H8 | LSFO | 268.4 | 22.3 | 30.1 | 37.9 | 45.6 | 53.4 | 10579 | 10667 | 10755 | 10843 | 11265 | 0.32 |  | 15.1% | 268.4 | 350.9162 | 434.1188 | 516.9323 | 601.5077 | 11.2642 | -0.00081086
| Honolulu_9 | H9 | LSFO | 279.6 | 22.3 | 30.3 | 38.4 | 46.4 | 54.4 | 10080 | 10433 | 10785 | 11138 | 11400 | 0.32 |  | 15.1% | 279.6 | 360.24 | 444.7473 | 531.0273 | 620.1313 | 11.3995 | -0.00052757
| Waiau_3 | W3 | LSFO | 295.5 | 22.3 | 28.4 | 34.5 | 40.5 | 46.6 | 9115 | 10150 | 11185 | 12220 | 11904 | 0.32 |  | 15% | 295.5 | 351.1015 | 413.0165 | 480.1265 | 554.6685 | 11.9028 | -0.0012425
| Waiau_4 | W4 | LSFO | 272.3 | 22.3 | 28.4 | 34.5 | 40.5 | 46.6 | 10904 | 11292 | 11680 | 12068 | 11832 | 0.32 |  | 12% | 272.3 | 338.8144 | 407.6956 | 477.7756 | 551.3904 | 11.8324 | 0.00041202
| Waiau_5 | W5 | LSFO | 273.7 | 22.5 | 30.5 | 38.5 | 46.5 | 54.5 | 10364 | 10840 | 11316 | 11791 | 11526 | 0.32 |  | 4.7% | 273.7 | 356.612 | 443.332 | 533.86 | 628.188 | 11.5264 | 0.00038532
| Waiau_6 | W6 | LSFO | 276.2 | 22.5 | 30.3 | 38 | 45.8 | 53.5 | 10399 | 10893 | 11388 | 11882 | 11618 | 0.32 |  | 4.7% | 276.2 | 357.3122 | 441.1883 | 530.0147 | 621.5061 | 11.6169 | -0.0010636
| Waiau_7 | W7 | LSFO | 316 | 27 | 41 | 55 | 68.9 | 82.9 | 9247 | 9794 | 10340 | 10887 | 10600 | 0.32 |  | 5.2% | 316 | 445.458 | 582.574 | 726.3 | 878.718 | 10.5997 | -0.00026538
| Waiau_8 | W8 | LSFO | 314.1 | 27 | 41.8 | 56.6 | 71.3 | 86.1 | 8971 | 9358 | 9746 | 10133 | 10204 | 0.32 |  | 5.2% | 314.1 | 446.8708 | 585.3692 | 728.6354 | 878.6038 | 10.2045 | 0.00045761
| Waiau_9 | W9 | Diesel | 245.3 | 5.9 | 17.7 | 29.4 | 41.2 | 52.9 | 8514 | 9199 | 9883 | 10568 | 13115 | 3.3738 | 99.19 | 10.9% | 245.3 | 345.7652 | 453.3935 | 570.0129 | 693.6585 | 13.1126 | -0.0023629
| Waiau_10 | W10 | Diesel | 234.7 | 5.9 | 16.9 | 27.9 | 38.9 | 49.9 | 7904 | 8529 | 9155 | 9780 | 12499 | 3.5552 | 99.19 | 10.9% | 234.7 | 321.644 | 415.463 | 516.168 | 623.748 | 12.5 | 0.00095992
| Kahe_1 | K1 | LSFO | 387.9 | 36.5 | 47.9 | 59.3 | 70.7 | 82.1 | 9237 | 9531 | 9825 | 10118 | 10101 | 0.32 |  | 3.6% | 387.9 | 493.2018 | 601.8552 | 713.8602 | 829.2054 | 10.0999 | -0.001056
| Kahe_2 | K2 | LSFO | 383.4 | 36.7 | 48.1 | 59.4 | 70.8 | 82.1 | 9365 | 9444 | 9524 | 9603 | 9915 | 0.32 |  | 3.6% | 383.4 | 490.161 | 596.8782 | 705.4518 | 813.9657 | 9.9143 | -0.00067966
| Kahe_3 | K3 | LSFO | 373.9 | 36.3 | 48.8 | 61.2 | 73.7 | 86.1 | 9030 | 9188 | 9345 | 9502 | 9703 | 0.32 |  | 5.2% | 373.9 | 486.775 | 600.7062 | 717.5187 | 835.3435 | 9.702 | -0.0009849
| Kahe_4 | K4 | LSFO | 390.5 | 36.3 | 48.6 | 60.8 | 73.1 | 85.3 | 9041 | 9221 | 9402 | 9582 | 9927 | 0.32 |  | 5.2% | 390.5 | 501.7043 | 614.2005 | 729.8451 | 846.7455 | 9.9267 | -0.00032356
| Kahe_5 | K5 | LSFO | 569.7 | 54.7 | 74.6 | 94.5 | 114.4 | 134.3 | 9012 | 9133 | 9254 | 9375 | 9691 | 0.32 |  | 3.2% | 569.7 | 749.0388 | 930.7855 | 1114.9401 | 1301.5026 | 9.691 | 9.6798e-06
| Kahe_6 | K6 | LSFO | 579.7 | 54 | 74.1 | 94.2 | 114.3 | 134.4 | 9142 | 9450 | 9759 | 10067 | 10059 | 0.32 |  | 2.1% | 579.7 | 763.4542 | 953.3992 | 1149.5551 | 1351.9018 | 10.0588 | -0.00020685
| Kalaeloa_CC1 | Kal1 | LSFO | 637.3 | 67 | 72.8 | 78.5 | 84.3 | 90 | 5725 | 5832 | 5939 | 6047 | 8585 | 6 |  | 1.5% | 637.3 | 670.505 | 703.7474 | 738.1936 | 772.6615 | 8.5851 | 0.00012778
| Kalaeloa_CC2 | Kal2 | LSFO | 637.3 | 67 | 72.8 | 78.5 | 84.3 | 90 | 5725 | 5832 | 5939 | 6047 | 8585 | 6 |  | 1.5% | 637.3 | 670.505 | 703.7474 | 738.1936 | 772.6615 | 8.5851 | 0.00012778
| Kalaeloa_CC3 | Kal3 | LSFO | 0.1 | 0 | 28 |  |  |  | 8651 |  |  |  | 8654 | 6 |  | 1.5% | 0.1 | 242.328 | 242.328 | 242.328 | 242.328 | 8.6546 | 0.00057143
| AES | AES | Coal | 1284.7 | 67 | 96.5 | 126 | 155.5 | 180 | 15805 | 16106 | 16407 | 16708 | 17314 | 2 |  | 1.5% | 1284.7 | 1750.9475 | 2226.0745 | 2710.081 | 3119.427 | 17.3301 | 0.01615
| H-Power | HPOWER | MSW | [11 empty] | 18 |  | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CIP_CT | CIP-CT1 | Biodiesel | 714.5 | 45 | 113 |  |  |  | 8915.3529 |  |  |  | 11688 | 40.76 |  | 15% | 714.5 | 1320.744 | 1320.744 | 1320.744 | 1320.744 | 11.688 | 0
| Airport_DSG | AiportDG | Biodiesel | 81.64 | 8 | [8 empty] | 10205 | 37.46 |  | 58% | 81.64 | 81.64 | 81.64 | 81.64 | 81.64 | 10.205 | 0
Note: horizontal block (technology_info) describes existing thermal technologies to add to technology and project tables (one-to-one); vertical block (build_info) describes build dates for those projects and others defined in PSIP workbook (costs should be provided if build date is earlier than costs in PSIP workbook)
Note: any values specified here set upper and lower bounds on construction in that year; this will lock in a building plan if applied during the study period.
gen_install_plan | load_zone | technology | site | orientation | build_year | proj_existing_cap | proj_overnight_cost | proj_fixed_om | latitude | longitude | retirement year | unit_size | substation_cost_per_kw | variable_o_m | forced_outage_rate | scheduled_outage_rate | fuel | heat_rate | intermittent | resource_limited | distributed | must_run | non_cycling | baseload | cogen | min_uptime | min_downtime | startup_energy
existing | Oahu | Honolulu_8 | na | na | 1954 | 53.4 | 530.5872 | 0 |  |  | 2021 | 53.4 | 0 | 0.32 | 0.151 | 0 | LSFO | 11265 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 190
existing | Oahu | Honolulu_9 | na | na | 1957 | 54.4 | 530.5872 | 0 |  |  | 2021 | 54.4 | 0 | 0.32 | 0.151 | 0 | LSFO | 11400 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 190
existing | Oahu | Waiau_3 | na | na | 1947 | 46.6 | 530.5872 | 0 |  |  | 2020 | 46.6 | 0 | 0.32 | 0.15 | 0 | LSFO | 11904 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 337
existing | Oahu | Waiau_4 | na | na | 1950 | 46.6 | 530.5872 | 0 |  |  | 2020 | 46.6 | 0 | 0.32 | 0.12 | 0 | LSFO | 11832 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 337
existing | Oahu | Waiau_5 | na | na | 1959 | 54.5 | 530.5872 | 0 |  |  | 2020 | 54.5 | 0 | 0.32 | 0.047 | 0 | LSFO | 11526 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 277
existing | Oahu | Waiau_6 | na | na | 1961 | 53.5 | 530.5872 | 0 |  |  | 2022 | 53.5 | 0 | 0.32 | 0.047 | 0 | LSFO | 11618 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 277
existing | Oahu | Waiau_7 | na | na | 1966 | 82.9 | 530.5872 | 0 |  |  | 2022 | 82.9 | 0 | 0.32 | 0.052 | 0 | LSFO | 10600 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933
existing | Oahu | Waiau_8 | na | na | 1968 | 86.1 | 530.5872 | 0 |  |  | 2022 | 86.1 | 0 | 0.32 | 0.052 | 0 | LSFO | 10204 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933
existing | Oahu | Waiau_9 | na | na | 1973 | 52.9 | 530.5872 | 0 |  |  | 2050 | 52.9 | 0 | 3.3738 | 0.109 | 0 | Diesel | 13115 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 36
existing | Oahu | Waiau_10 | na | na | 1973 | 49.9 | 530.5872 | 0 |  |  | 2050 | 49.9 | 0 | 3.5552 | 0.109 | 0 | Diesel | 12499 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 33
existing | Oahu | Kahe_1 | na | na | 1963 | 82.1 | 530.5872 | 0 |  |  | 2022 | 82.1 | 0 | 0.32 | 0.036 | 0 | LSFO | 10101 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933
existing | Oahu | Kahe_2 | na | na | 1964 | 82.1 | 530.5872 | 0 |  |  | 2022 | 82.1 | 0 | 0.32 | 0.036 | 0 | LSFO | 9915 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933
existing | Oahu | Kahe_3 | na | na | 1970 | 86.1 | 530.5872 | 0 |  |  | 2022 | 86.1 | 0 | 0.32 | 0.052 | 0 | LSFO | 9703 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933
existing | Oahu | Kahe_4 | na | na | 1972 | 85.3 | 530.5872 | 0 |  |  | 2022 | 85.3 | 0 | 0.32 | 0.052 | 0 | LSFO | 9927 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933
existing | Oahu | Kahe_5 | na | na | 1974 | 134.3 | 530.5872 | 0 |  |  | 2045 | 134.3 | 0 | 0.32 | 0.032 | 0 | LSFO | 9691 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 1352
existing | Oahu | Kahe_6 | na | na | 1981 | 134.4 | 530.5872 | 0 |  |  | 2045 | 134.4 | 0 | 0.32 | 0.021 | 0 | LSFO | 10059 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 2703
existing | Oahu | Kalaeloa_CC1 | na | na | 1989 | 90 | 1850 | 0 |  |  | 2050 | 90 | 0 | 6 | 0.015 | 0 | LSFO | 8585 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 5 | 800
existing | Oahu | Kalaeloa_CC2 | na | na | 1991 | 90 | 1850 | 0 |  |  | 2052 | 90 | 0 | 6 | 0.015 | 0 | LSFO | 8585 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 800
existing | Oahu | Kalaeloa_CC3 | na | na | 1991 | 28 | 1850 | 0 |  |  | 2052 | 28 | 0 | 6 | 0.015 | 0 | LSFO | 8654 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0
existing | Oahu | AES | na | na | 1992 | 180 | 1850 | 0 |  |  | 2022 | 180 | 0 | 2 | 0.015 | 0 | Coal | 17314 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 24 | 24 | 0
existing | Oahu | H-Power | na | na | 1989 | 73 | 1850 | 0 |  |  | 2050 | 73 | 0 | 18 | 0.1 | 0.4137 | MSW | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0
existing | Oahu | CIP_CT | na | na | 2009 | 113 | 530.5872 | 0 |  |  | 2070 | 113 | 0 | 40.76 | 0.15 | 0 | Biodiesel | 11688 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 126
existing | Oahu | Airport_DSG | na | na | 2013 | 8 | 530.5872 | 0 |  |  | 2074 | 8 | 0 | 37.46 | 0.58 | 0 | Biodiesel | 10205 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 126
existing | Oahu | OnshoreWind |  |  | 2011 | 30 | 2190.1816 | 0 | 21.682 | -157.976
existing | Oahu | OnshoreWind |  |  | 2012 | 69 | 2190.1816 | 0 | 21.62 | -158.048
existing | Oahu | CentralTrackingPV |  |  | 2012 | 5 | 2915.9052 | 0 | 21.32 | -158.0869
existing | Oahu | CentralTrackingPV |  |  | 2016 | 27.6 | 2915.9052 | 0 | 21.4619 | -158.1893
existing | Oahu | FlatDistPV |  |  | 2016 | 180.264 | 4207.7087 | 0
existing | Oahu | SlopedDistPV |  |  | 2016 | 263.736 | 6126.9116 | 0
existing | Oahu | IC_Schofield | na | na | 2018 | 48.84
existing | Oahu | CentralTrackingPV |  |  | 2019 | 49 |  |  | 21.6363 | -158.0608
existing | Oahu | CentralTrackingPV |  |  | 2019 | 14.7 |  |  | 21.4262 | -158.0185
existing | Oahu | CentralTrackingPV |  |  | 2019 | 45.9 |  |  | 21.4306 | -157.9946
existing | Oahu | CentralTrackingPV |  |  | 2019 | 20 |  |  | 21.3376 | -158.0107
Note: the rows below are unused; these were moved back into the PSIP module.
Oahu DistPV construction calculations, assuming 20-year life |  |  |  | see p. 3-8 of PSIP 2016-12-23 vol. 1. for 20-year life and discussion of reconstruction at retirement (focused on utility-scale, but we assume it applies to DG; also Resolve applied these as set levels).
year | non-controllable | controllable | total level | retirements | additions |  | All-islandPV level forecast from H-1 of PSIP 2016-12-23 and xx | Approx. Oahu PV level from Figure J-10 of 2016-12-23 PSIP (excl FIT(?))
2016 | 180.264 | 0 | 180.264 | 0 |  |  | 471 | 400 |  | DistPV installations
2020 | 606.3 | 0 | 606.3 | 0 | 426.036 |  | 856 | 600 |  | (2020, "DistPV", 426.036),
2022 | 606.3 | 74 | 680.3 | 0 | 74 |  |  |  |  | (2022, "DistPV", 74),
2025 | 606.3 | 138.6 | 744.9 | 0 | 64.6 |  | 1169 | 720 |  | (2025, "DistPV", 64.6),
2030 | 606.3 | 262.4 | 868.7 | 0 | 123.8 |  |  | 865 |  | (2030, "DistPV", 123.8),
2035 | 606.3 | 409.1 | 1015.4 | 0 | 146.7 |  |  | 1020 |  | (2035, "DistPV", 146.7),
2040 | 606.3 | 557.1 | 1163.4 | 426.036 | 574.036 |  | 1517 | 1160 |  | (2040, "DistPV", 574.036),
2045 | 606.3 | 701.6 | 1307.9 | 138.6 | 283.1 |  | 1697 | 1300 |  | (2045, "DistPV", 283.1),
optional replacements at retirement (pasted into PSIP module)
(2011, "OnshoreWind", 30),
(2012, "OnshoreWind", 69),
(2012, "CentralTrackingPV", 5),
(2016, "CentralTrackingPV", 27.6),
(2016, "FlatDistPV", 180.264),
(2018, "IC_Schofield", 48.84),
(2019, "CentralTrackingPV", 49),
(2019, "CentralTrackingPV", 14.7),
(2019, "CentralTrackingPV", 45.9),
(2019, "CentralTrackingPV", 20),
TODO: re-import HECO generator info with 20 year life for renewables
TODO: make sure import code can handle multiple batches of the same technology in the same year, with or without different locations (or none at all)
TODO: convert LoadShiftBattery to some standard tech (check what HECO assumed)
TODO: no reserves from LoadShiftBattery in PSIP?
TODO: any contingency or regulation battery in PSIP?
TODO: allow central PV and wind without lat lon specified (just require a certain total amount from any appropriate project)
TODO: switch to using 4-hour and 6-hour batteries, and fix up LoadShiftBattery
TODO: add project size and cap factors for West Loch PV (on Pearl Harbor land) (eventually; can use nearest ag land solar for now)
TODO: add gen_install_plan to scenario_data (default is "existing"); then we can include PSIP_DistPV to follow the forecast or exclude it to allow free selection of PV
note: project build data will get stored in one built_project table,but scenario_data.py will extract it into proj_existing_builds.tab and proj_build_costs.tab
Notes:
Honua was removed because the company behind it went bankrupt in Feb. 2016 without completing the project. see:
Star-Advertiser "Pulling the Plug", 2016-02-08, http://www.pressreader.com/usa/honolulu-star-advertiser/20160208/281848642645296
http://www.ct-si.org/events/APCE2011/sld/pdf/9.pdf
http://oeqc.doh.hawaii.gov/Shared%20Documents/EA_and_EIS_Online_Library/Oahu/2010s/2010-04-08-OA-FEA-Honua-Power.pdf
TODO:
report reserves provided by each source
jdfvbkmnjjjuhjuhnbvcxzp,lmpn/////[
.,?"P}o?P<K?"<K?"op]k?"PKOP']/K<"}¦OPKPO"}<K?"KL,l?"LK?"K<">K?">L
TODO later:
add code to support non_cycling flag in switch unit commitment
limit Airport DSG to 1500 hours/year
add Tesoro cogen plant (built in 1983; assume 61-year life)
add Chevron cogen plant (G1-G3 built in 1990, G4 built in 2011; assume 61-year life)
fill in capital costs for all plants (use original cost, converted to 2016$; this reflects the fact that payments escalate with inflation in switch)
get better fixed and variable O&M for all plants
In Ulupono scenarios, switch wind and solar to 35-year life to avoid retirement and replacement by 2045
include pumped storage in reserve requirements and provision
allow specification of O&M per hour (based on commitment), rather than just per MWh (based on dispatch)
create flag for cost-only projects (not committed/dispatched, just built/retired)
convert batteries, hydrogen, evs? and fuel market expansion into projects with side constraints imposed by modules
define multiple speeds of regulating reserve product, with separate targets at each speed (to account for renewable mis-forecast)
(we don't define a contingency reserve product for extreme misforecasts, because it is hard to bound the quantity, and it can be a slow-start product (not instant-start), and most likely it would be addressed by rolling blackouts, not dipping into n-1 reserves)
allow users to specify a "greenfield" model, omitting all previous builds (in scenario_data.py)
Note on P16: converted hourly cost to cost per MWh, assuming operation in middle of range
Note on P17: converted hourly cost to cost per MWh, assuming operation in middle of range
Note on P24: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on J27: Changed from 185 to 180 to match GE RPS Study (http://www.hnei.hawaii.edu/projects/hawaii-rps-study) and EIA form 860 data for 2017.
Note on P27: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on E28: Removed heat rate (74014!) because it runs on waste, which is a non-fuel in SWITCH-Hawaii.
Note on G28: removed 73 MW operating point because we don't use a heat rate curve for MSW (treat as non-fuel energy source)
Note on P28: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on C29: This is Siemens SGT6-3000E per final order in docket 2005-0145
Note on K29: Assigned a value to make consistent with full-load heat rate
Note on E30: Changed from 40.8 to be consistent with 8 MW min/max load and 10,205 full load heat rate
Note on F30: Changed from 0 because HECO can only run gen at 8 MW (and only 1500 h/y) per application (p. 23) in docket 2008-0329
Note on K30: removed 10,205 from here because it has no corresponding power point
Note on F34: from EIA 860 or 923 database unless otherwise noted
Note on G34: Despite the name, this is actually the amount of capacity added in each project in the specified year.
Note on H34: $/kW, should be omitted if technology and build_year are covered by the new generator costs workbook
Note on I34: $/kW-year Should be omitted if technology and build_year are covered by the new generator costs workbook
Note on J34: If latitude and longitude are specified, they are used to match existing renewable projects to available resources and/or to calculate spur line cost to interconnect; if omitted, spur line cost will be assumed 0.
Note on L34: from 2016-12-23 PSIP, Book 1, pp. 4-3 - 4-4 (E3 Plan) unless otherwise noted
Note on S34: full load heat rate, Btu/kWh
Note on W34: closest match to HECO's definition of "baseload" -- must be committed, but level can be adjusted. from Hawaii RPS Study, GE Energy Management Energy Consulting. 8.2 Thermal Generating Characteristics, Table 7: Thermal Generating Unit Properties
Note on X34: Must be fully committed or fully non-committed during each timeseries (day)
Note on Y34: forces dispatch at 100% unless otherwise specified
Note on AA34: From GE Hawaii RPS Study for HNEI, 2015, https://www.hnei.hawaii.edu/projects/hawaii-rps-study
Note on AB34: From GE Hawaii RPS Study for HNEI, 2015, https://www.hnei.hawaii.edu/projects/hawaii-rps-study
Note on AC34: MMBtu, for whole unit Used hot values from Hawaii RPS Study
Note on H35: $/kW; 2016 annual report says total ratebase is $1386000000, which is about half generation, so we set value per kW accordingly
Note on L43: set to 2050 since the plan says it will switch to biodiesel in 2045
Note on L44: set to 2050 since the plan says it will switch to biodiesel in 2045
Note on H51: set to to roughly match cost of new CC plant and interconnect from PSIP 2016-12
Note on L51: set to 61 years, based on average age of already-scheduled retirements
Note on L52: set to 61 years, based on average age of already-scheduled retirements
Note on L53: set to 61 years, based on average age of already-scheduled retirements
Note on L54: set to 30 years (expiry of initial PPA) starting 2019-10-01 because there is no support from PUC, HECO or stakeholders for continuing with coal and continuing with biomass is economically marginal (biomass could burn as well in HECO plants and that's probably easier politically, but we don't generally consider that option).
Note on AA54: AES PPA states that HECO must reimburse resetart costs if plant operation is suspended more than 5 times in a year. Implied plant must run for long periods at a atime, so we set it to 24 hours.
Note on AB54: AES PPA states that HECO must reimburse resetart costs if plant operation is suspended more than 5 times in a year. Implied plant must run for long periods at a atime, so we set it to 24 hours.
Note on C55: note: nameplate capacity is 97.3 MW and winter/summer capacity are 86.0 MW per EIA form 860M for September 2016
Note on G55: note: nameplate capacity is 97.3 MW and winter/summer capacity are 86.0 MW per EIA form 860M for September 2016
Note on L55: set to 61 years, based on average age of already-scheduled retirements
Note on Q55: 42.8 MW baseload operation per monthly and annual avg production in EIA form 923 for 2015
Note on AA55: Treated as zero, since it runs all the time.
Note on AB55: Treated as zero, since it runs all the time.
Note on AC55: Treated as variable plant instead of fuel-based gen, so startup fuel must be omitted.
Note on L56: set to 61 years, based on average age of already-scheduled retirements
Note on C57: "Airport Dispatchable Standby Generation" (docket 2008-0329)
Note on F57: planned for late 2013 according to https://puc.hawaii.gov/wp-content/uploads/2015/04/Adequacy-of-Supply-HECO-2013.pdf
Note on L57: set to 61 years, based on average age of already-scheduled retirements
Note on C58: Kahuku wind farm
Note on D58: site and orientation for existing renewable projects will be looked up in import_data.py
Note on E58: site and orientation for existing renewable projects will be looked up in import_data.py
Note on H58: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on J58: found via Google Maps search
Note on C59: Kawailoa Wind Farm
Note on D59: site and orientation for existing renewable projects will be looked up in import_data.py
Note on E59: site and orientation for existing renewable projects will be looked up in import_data.py
Note on H59: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on J59: found via Google Maps search
Note on C60: Kalaeloa Solar 2 (5 MW PV) (KAS1 was canceled) should be CentralFixedPV, but we don't generally activate that, so this will do
Note on D60: site and orientation for existing renewable projects will be looked up in import_data.py
Note on E60: site and orientation for existing renewable projects will be looked up in import_data.py
Note on H60: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on J60: location from EIA form 860M database (September 2016)
Note on C61: Waianae Solar (Eurus) from PSIP 2016-04-01; matched to specific project with query below
Note on D61: site and orientation for existing renewable projects will be looked up in import_data.py
Note on E61: site and orientation for existing renewable projects will be looked up in import_data.py
Note on H61: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on J61: Mauka of Kamaile academy according to http://eurusenergy.com/news/press-releases/eurus-energy-america/waianae-solar-project-construction-financing/
Note on G62: 444 MW DistPV installed by 2016 according to PSIP 2016-04-01 Figure J-19; we apportion between flat and sloped roofs based on the shares shown for Oahu in Google Sunroof data (see top of solar_resources.py).
Note on H62: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on G63: 444 MW DistPV installed by 2016 according to PSIP 2016-04-01 Figure J-19; we apportion between flat and sloped roofs based on the shares shown for Oahu in Google Sunroof data (see top of solar_resources.py).
Note on H63: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on C64: profile copied from PSIP 2016-12 generator and storage data.xlsx
Note on C65: Kawailoa Solar, formerly SunEdison project
Note on F65: from https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board
Note on J65: From xx (view source for map marker)
Note on C66: Lanikuhana Solar (Mililani Solar), formerly SunEdison
Note on F66: from https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board
Note on J66: from page source of http://energy.ehawaii.gov/epd/public/energy-project-details.html?rid=f1-3b2df53a54d8c6d3
Note on C67: Waipio (Waiawa) PV, formerly SunEdison
Note on F67: from https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board
Note on J67: from page source of http://energy.ehawaii.gov/epd/public/energy-project-details.html?rid=f7-3f29f31d354cf91d
Note on C68: West Loch PV
Note on F68: Seems like half of it came online in 2017 (or maybe it was some other project at JBPHH?), and all of it was expected to be online in 2018. See https://www.bizjournals.com/pacific/news/2017/04/28/navy-launches-operations-of-pearl-harbor-solar.html and https://dailyenergyinsider.com/news/10294-hawaiian-electric-companies-reports-100-megawatts-solar-installed-across-service-territories-2017/ But according to https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board (accessed 10/22/19) it will be online in 2019.
Note on G68: This is 28 MW DC, 20 MW AC. See PSIP 2016-12-23 and these links: https://www.hawaiianelectric.com/navy-hawaiian-electric-plan-large-solar-project-on-joint-base-pearl-harbor-hickam (most authoritative) https://dailyenergyinsider.com/news/10294-hawaiian-electric-companies-reports-100-megawatts-solar-installed-across-service-territories-2017/ http://greenfleet.dodlive.mil/files/2016/09/JB-Pearl-Harbor-Hickam-Factsheet.pdf https://www.bizjournals.com/pacific/news/2017/04/28/navy-launches-operations-of-pearl-harbor-solar.html
Note on J68: from Pearl Harbor Hickam Solar Project fact sheet at http://greenfleet.dodlive.mil/files/2016/09/JB-Pearl-Harbor-Hickam-Factsheet.pdf
Note on C75: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B76: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C76: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B77: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C77: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B78: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C78: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B79: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C79: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B80: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C80: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B81: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C81: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B82: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C82: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on A143: 444 MW DistPV installed by 2016 according to PSIP 2016-04-01 Figure J-19