## info
TODO: create separate projects and technologies for each vintage year (or maybe 5-year period), and then model improvements in performnce of newly installed renewable techs over time and degradation after installation.
technologies
technology | tech_scen_id | min_vintage_year | unit_size | substation_cost_per_kw | variable_o_m_per_mwh | fuel | full_load_heat_rate | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | resource_limited | distributed | baseload | must_run | non_cycling | cogen | gen_storage_efficiency | gen_storage_energy_to_power_ratio | gen_storage_max_cycles_per_year
CC_152 | all | 2016 | 150.586 | 154.7289 | 4.49 | LSFO | 7121.9196 | 30 | 1.6% | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
IC_MCBH | all | 2016 | 9.1639 | 498.3344 | 20.96 | LSFO | 8674.0184 | 30 | 2% | 2% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
IC_Schofield | all | 2016 | 8.14 | 309.1728 | 20.96 | LSFO | 8772.4141 | 30 | 2% | 2% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
IC_Barge | all | 2016 | 16.7864 | 160.8446 | 20.96 | LSFO | 8526.3548 | 30 | 2% | 2% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
Lake_Wilson | all | 2016 | 150 | 435.8333 | 0 | Hydro | 0 | 50 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.77 | 24 | 1000
OnshoreWind | PSIP_2016_12 | 2016 | NA | 456.6667 | 0 | WND | 0 | 20 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
OffshoreWind | PSIP_2016_12 | 2016 | NA | 512.5 | 0 | WND | 0 | 20 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
CentralFixedPV | PSIP_2016_12 | 2016 | NA | 415 | 0 | SUN | 0 | 20 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
CentralTrackingPV | PSIP_2016_12 | 2016 | NA | 415 | 0 | SUN | 0 | 20 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
FlatDistPV | PSIP_2016_12 | 2016 | NA | 0 | 0 | SUN | 0 | 20 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
SlopedDistPV | PSIP_2016_12 | 2016 | NA | 0 | 0 | SUN | 0 | 20 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
Battery_Conting | PSIP_2016_12 | 2016 | NA | 153 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0 | NA
Battery_Reg | PSIP_2016_12 | 2016 | NA | 153 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0 | NA
Battery_4 | PSIP_2016_12 | 2016 | NA | 153 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 4 | 365
Battery_6 | PSIP_2016_12 | 2016 | NA | 153 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 6 | 365
Battery_Conting | ATB_2019_low | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90% | 0 | NA
Battery_Reg | ATB_2019_low | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90% | 0 | NA
Battery_Bulk | ATB_2019_low | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90% | NA | 365
OnshoreWind | ATB_2019_low | 2018 | NA | 0 | 0 | WND | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
OffshoreWind | ATB_2019_low | 2018 | NA | 0 | 0 | WND | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
CentralTrackingPV | ATB_2019_low | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
FlatDistPV | ATB_2019_low | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
SlopedDistPV | ATB_2019_low | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
Battery_Conting | ATB_2019_mid | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | NA
Battery_Reg | ATB_2019_mid | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | NA
Battery_Bulk | ATB_2019_mid | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | NA | 365
OnshoreWind | ATB_2019_mid | 2018 | NA | 0 | 0 | WND | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
OffshoreWind | ATB_2019_mid | 2018 | NA | 0 | 0 | WND | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
CentralTrackingPV | ATB_2019_mid | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
FlatDistPV | ATB_2019_mid | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
SlopedDistPV | ATB_2019_mid | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
Battery_Conting | ATB_2019_high | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | NA
Battery_Reg | ATB_2019_high | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | NA
Battery_Bulk | ATB_2019_high | 2018 | NA | 0 | 0 | Battery | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | NA | 365
OnshoreWind | ATB_2019_high | 2018 | NA | 0 | 0 | WND | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
OffshoreWind | ATB_2019_high | 2018 | NA | 0 | 0 | WND | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
CentralTrackingPV | ATB_2019_high | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA
FlatDistPV | ATB_2019_high | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
SlopedDistPV | ATB_2019_high | 2018 | NA | 0 | 0 | SUN | 0 | 30 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | NA | NA | NA
CC_383 | NA | 2016 |  | 383 | 1.085 | 40.3786 | 1.085 | LSFO | 6965 | 30 | 1.6% | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT_100 | NA | 2016 |  | 100 | 12.99 | 9.01 | 12.99 | LSFO | 10849 | 30 | 1.6% | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0
non-resource-limited project definitions (note: only projects with technologies with the right tech_scen_id will be used in each case, so duplicates here will be dropped)
load_zone | technology | site | orientation | max_capacity |  | max projects allowed | nominal project capacity
Oahu | CC_152 | na | na | 1505.86 |  | 10 | 150.586
Oahu | IC_MCBH | na | na | 274.9158 |  | 10 | 27.4916
Oahu | IC_Schofield | na | na | 48.84 |  | 1 | 48.84
Oahu | IC_Barge | na | na | 1007.1835 |  | 10 | 100.7184
Oahu | Battery_Conting | na | na | 3000 |  | 1 | 3000
Oahu | Battery_Reg | na | na | 3000 |  | 1 | 3000
Oahu | Battery_4 | na | na | 3000 |  | 1 | 3000
Oahu | Battery_6 | na | na | 3000 |  | 1 | 3000
Oahu | Battery_Bulk | na | na | 3000 |  | 1 | 3000
Oahu | Lake_Wilson | na | na | 150 |  | 1 | 150
Transmission cost per MW-km from project to load center
1000
Note on B5: if tech_scen_id is all, it will be used across all scenarios.
Note on D5: Use NA for small, modular technologies
Note on B6: We use PSIP thermal plants for all technology scenarios because they are mature, with fairly certain costs, already assessed by HECO.
Note on I6: Assumed 30 years for thermal plants, per e-mail from Todd Kanja at HECO 2016-05-05 (he said this is their assumption for PSIP). Also see "data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/technologies.tab"
Note on J6: From PSIP p. D-28
Note on K6: From PSIP p. D-28
Note on I7: Assumed 30 years for thermal plants, per e-mail from Todd Kanja at HECO 2016-05-05 (he said this is their assumption for PSIP). Also see "data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/technologies.tab"
Note on J7: From HECO New Resource Assumptions spreadsheet
Note on K7: From HECO New Resource Assumptions spreadsheet
Note on I8: Assumed 30 years for thermal plants, per e-mail from Todd Kanja at HECO 2016-05-05 (he said this is their assumption for PSIP). Also see "data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/technologies.tab"
Note on J8: From HECO New Resource Assumptions spreadsheet
Note on K8: From HECO New Resource Assumptions spreadsheet
Note on I9: Assumed 30 years for thermal plants, per e-mail from Todd Kanja at HECO 2016-05-05 (he said this is their assumption for PSIP). Also see "data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/technologies.tab"
Note on J9: From HECO New Resource Assumptions spreadsheet
Note on K9: From HECO New Resource Assumptions spreadsheet
Note on A10: Data from John Wehrheim, Pacific Hydro, summer 2015
Note on J10: Not specified, assumed 0
Note on K10: Not specified, assumed 0
Note on I11: assumed 20 for renewables per p. 3-8 of PSIP 2016-12-23 vol. 1. Also see "data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/technologies.tab"
Note on J11: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J12: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J13: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J14: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J15: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J16: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on J17: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on K17: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on S17: all assumed equivalent to 4-hour and commercial load-shifting (assume balancing battery can be configured similarly with specified cost structure)
Note on U17: assume no limit on cycling-oriented batteries
Note on J19: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on K19: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on U19: from storage worksheet
Note on E20: Set equal to other PSIP battery projects because smaller size and higher cost only for 6-hour battery seems artificial
Note on J20: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on K20: No outage rate specified in HECO New Resource Assumptions workbook; assumed 0
Note on E21: Not clear whether ATB capex includes interconnect cost for storage technologies; we assume it does and/or that interconnect cost is minimal, since storage is sited at RE site, substation or customer, wherever it minimizes congestion most effectively.
Note on S21: From specifications for reference storage system in ATB workbook, https://data.nrel.gov/files/89/2018-ATB-data-interim-geo.xlsm, originally from cole_utility-scale_2016 http://dx.doi.org/10.1109/NAPS.2016.7747866
Note on U21: assume no limit on cycling-oriented batteries
Note on S22: From specifications for reference storage system in ATB workbook, https://data.nrel.gov/files/89/2018-ATB-data-interim-geo.xlsm, originally from cole_utility-scale_2016 http://dx.doi.org/10.1109/NAPS.2016.7747866
Note on U22: assume no limit on cycling-oriented batteries
Note on S23: From specifications for reference storage system in ATB workbook, https://data.nrel.gov/files/89/2018-ATB-data-interim-geo.xlsm, originally from cole_utility-scale_2016 http://dx.doi.org/10.1109/NAPS.2016.7747866
Note on U23: Assumed to have similar performance to HECO model (365 is really the minimum usable amount for bulk storage)
Note on E24: ATB CAPEX includes substation costs; see https://atb.nrel.gov/electricity/2018/index.html?t=lw&s=cx and https://atb.nrel.gov/electricity/2018/index.html?t=ow&s=cx
Note on J24: Assumed to be included in performance data; see https://atb.nrel.gov/electricity/2018/index.html?t=lw
Note on E25: ATB CAPEX includes generic connection costs; see https://atb.nrel.gov/electricity/2018/index.html?t=lw&s=cx and https://atb.nrel.gov/electricity/2018/index.html?t=ow&s=cx
Note on J25: Assumed to be included in performance data; see https://atb.nrel.gov/electricity/2018/index.html?t=lw
Note on E26: ATB CAPEX includes generic connection costs; see https://atb.nrel.gov/electricity/2018/index.html?t=lw&s=cx and https://atb.nrel.gov/electricity/2018/index.html?t=ow&s=cx
Note on J26: Assumed to be included in performance data; see https://atb.nrel.gov/electricity/2018/index.html?t=lw
Note on J27: Assumed to be included in performance data; see https://atb.nrel.gov/electricity/2018/index.html?t=lw
Note on J28: Assumed to be included in performance data; see https://atb.nrel.gov/electricity/2018/index.html?t=lw
Note on A48: omitted due to difficulty modeling commitment
Note on J48: From 2016-04-01 PSIP, p. D-29
Note on L48: From PSIP p. D-28
Note on M48: From PSIP p. D-28
Note on A49: omitted because heat rate and other details are not provided by HECO, and probably unattractive vs. CC and IC
Note on J49: Assumed same as for CC 152 and CC 383 operating in CT-only mode (in HECO New Resource Assumptions spreadsheet).
Note on L49: From PSIP p. D-28
Note on M49: From PSIP p. D-28
Note on E53: This must be specified to support allocation of generation among fuels via big-M constraint.
Note on G53: This must be specified to support allocation of generation among fuels via big-M constraint.

## annual costs
[15 empty] | formulas change here | [24 empty] | for analysis (not imported)
[15 empty] | >>> | <<<
technology | CC_152 | IC_MCBH | IC_Schofield | IC_Barge | Lake_Wilson | OnshoreWind | OffshoreWind | CentralFixedPV | CentralTrackingPV | FlatDistPV | SlopedDistPV | Battery_Conting | Battery_Reg | Battery_4 | Battery_6 | CentralTrackingPV | CentralTrackingPV | CentralTrackingPV | FlatDistPV | FlatDistPV | FlatDistPV | SlopedDistPV | SlopedDistPV | SlopedDistPV | OnshoreWind | OnshoreWind | OnshoreWind | OffshoreWind | OffshoreWind | OffshoreWind | Battery_Bulk | Battery_Bulk | Battery_Bulk | Battery_Conting | Battery_Conting | Battery_Conting | Battery_Reg | Battery_Reg | Battery_Reg |  | capital cost | annual capital | annual total
tech_scen_id | all | all | all | all | all | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | lake wilson | 3033 | 192.4265 | 192.4265
cost_base_year | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017
capital cost (base-year $ per kW) | [14 empty] | >>> | <<<
technology | CC_152 | IC_MCBH | IC_Schofield | IC_Barge | Lake_Wilson | OnshoreWind | OffshoreWind | CentralFixedPV | CentralTrackingPV | FlatDistPV | SlopedDistPV | Battery_Conting | Battery_Reg | Battery_4 | Battery_6 | CentralTrackingPV | CentralTrackingPV | CentralTrackingPV | FlatDistPV | FlatDistPV | FlatDistPV | SlopedDistPV | SlopedDistPV | SlopedDistPV | OnshoreWind | OnshoreWind | OnshoreWind | OffshoreWind | OffshoreWind | OffshoreWind | Battery_Bulk | Battery_Bulk | Battery_Bulk | Battery_Conting | Battery_Conting | Battery_Conting | Battery_Reg | Battery_Reg | Battery_Reg
tech_scen_id | all | all | all | all | all | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | year | battery_bulk (mid cost)
2017 | 1653.2417 | 3162.0825 | 2481.336 | 1323.1827 | 2800 | 2459.3294 | 6205.5985 | 2580.1783 | 2856.2574 | 3650.2947 | 3650.2947 | 679.7642 | 981.336 | 2414.5383 | 2907.6621 | 1821.5975 | 1821.5975 | 1821.5975 | 3008.3404 | 3008.3404 | 3008.3404 | 4486.9711 | 4486.9711 | 4486.9711 | 2173.6466 | 2173.6466 | 2173.6466 | 7468.2398 | 7468.2398 | 7468.2398 | 855 | 855 | 855 | 985.625 | 985.625 | 985.625 | 1116.25 | 1116.25 | 1116.25 | 2017 | 3206.25 | 330.1244 | 367.2337
2018 | 1637.5188 | 3124.5055 | 2451.9359 | 1322.9453 | 2800 | 2357.0724 | 6009.0653 | 2458.1608 | 2721.184 | 3447.7634 | 3447.7634 | 608.8829 | 881.9636 | 2181.7501 | 2627.5566 | 1828.1984 | 1828.1984 | 1828.1984 | 2932.2223 | 2932.2223 | 2932.2223 | 4276.4717 | 4276.4717 | 4276.4717 | 2123.2201 | 2136.4903 | 2173.6466 | 5759.9917 | 7199.9896 | 7468.2398 | 855 | 855 | 855 | 985.625 | 985.625 | 985.625 | 1116.25 | 1116.25 | 1116.25 | 2018 | 3206.25 | 330.1244 | 367.2337
2019 | 1630.366 | 3109.0701 | 2439.8617 | 1323.2506 | 2800 | 2301.0733 | 5812.5321 | 2354.1197 | 2606.0105 | 3276.8461 | 3276.8461 | 550.7225 | 799.0689 | 1985.8237 | 2391.5194 | 1577.0319 | 1796.0236 | 1828.1984 | 2158.9664 | 2790.472 | 2932.2223 | 3800.6269 | 4172.0188 | 4276.4717 | 2072.7937 | 2099.3339 | 2173.6466 | 5554.0718 | 6942.5897 | 7468.2398 | 762.1036 | 797.3107 | 855 | 878.5361 | 919.1221 | 985.625 | 994.9685 | 1040.9334 | 1116.25 | 2019 | 2989.9151 | 307.8499 | 342.4554
2020 | 1622.0231 | 3090.4103 | 2424.6545 | 1323.1314 | 2800 | 2309.4754 | 5615.999 | 2264.0878 | 2506.3452 | 3128.5865 | 3128.5865 | 501.8774 | 728.1413 | 1813.8353 | 2184.4238 | 1479.6514 | 1762.2555 | 1828.1984 | 2021.6089 | 2629.0446 | 2932.2223 | 3591.5924 | 4067.5659 | 4276.4717 | 2022.3672 | 2062.1776 | 2173.6466 | 5356.4732 | 6695.5915 | 7468.2398 | 669.2071 | 739.6214 | 855 | 771.4471 | 852.6191 | 978.3002 | 873.6871 | 965.6168 | 1101.6005 | 2020 | 2773.5802 | 285.5755 | 317.6771
2021 | 1615.2949 | 3075.097 | 2412.881 | 1323.5174 | 2800 | 2305.3286 | 5377.7769 | 2188.1463 | 2422.2779 | 3004.6679 | 3004.6679 | 462.8195 | 674.1066 | 1688.4679 | 2033.2958 | 1424.2912 | 1729.0054 | 1828.1984 | 1818.9533 | 2591.8013 | 2932.2223 | 3362.5567 | 3888.9854 | 4276.4717 | 1971.9407 | 2025.0212 | 2173.6466 | 5166.8519 | 6458.5649 | 7468.2398 | 618.104 | 703.1599 | 855 | 712.5366 | 810.5871 | 976.3101 | 806.9692 | 918.0143 | 1097.6202 | 2021 | 2636.8495 | 271.4973 | 302.0164
2022 | 1608.2974 | 3060.2575 | 2400.7657 | 1323.476 | 2800 | 2323.6829 | 5139.5549 | 2118.183 | 2344.8286 | 2891.3414 | 2891.3414 | 429.4783 | 627.1461 | 1581.3427 | 1904.7992 | 1368.931 | 1693.9081 | 1828.1984 | 1757.2194 | 2531.911 | 2932.2223 | 3133.521 | 3710.4048 | 4276.4717 | 1921.5142 | 1987.8648 | 2173.6466 | 4984.8782 | 6231.0977 | 7468.2398 | 567.0009 | 666.6984 | 855 | 653.6261 | 768.555 | 974.3199 | 740.2512 | 870.4117 | 1093.6399 | 2022 | 2500.1188 | 257.4191 | 286.3557
2023 | 1600.1598 | 3043.2162 | 2387.442 | 1323.0224 | 2800 | 2333.5769 | 4901.3329 | 2054.7827 | 2274.6444 | 2789.0265 | 2789.0265 | 401.5845 | 587.8138 | 1488.9518 | 1793.4499 | 1313.5709 | 1658.8108 | 1828.1984 | 1695.4856 | 2472.0206 | 2932.2223 | 2904.4854 | 3531.8243 | 4276.4717 | 1871.0877 | 1950.7085 | 2173.6466 | 4810.2358 | 6012.7947 | 7468.2398 | 515.8979 | 630.2368 | 855 | 594.7156 | 726.523 | 972.3298 | 673.5333 | 822.8092 | 1089.6596 | 2023 | 2363.3881 | 243.341 | 270.695
2024 | 1591.8072 | 3023.2198 | 2372.1048 | 1323.038 | 2800 | 2332.6805 | 4829.8663 | 1997.4322 | 2211.1575 | 2697.2288 | 2697.2288 | 377.1439 | 553.1443 | 1408.8707 | 1696.7138 | 1258.2107 | 1623.7134 | 1828.1984 | 1633.7518 | 2412.1303 | 2932.2223 | 2675.4497 | 3353.2437 | 4276.4717 | 1820.6613 | 1913.5521 | 2173.6466 | 4642.6219 | 5803.2774 | 7468.2398 | 464.7948 | 593.7753 | 855 | 535.8051 | 684.491 | 970.3396 | 606.8154 | 775.2066 | 1085.6792 | 2024 | 2226.6574 | 229.2628 | 255.0343
2025 | 1583.2496 | 3003.8307 | 2357.4152 | 1323.4911 | 2800 | 2317.92 | 4758.3997 | 1945.5071 | 2153.6763 | 2612.9154 | 2612.9154 | 355.997 | 522.9238 | 1338.8211 | 1612.2063 | 1202.8505 | 1588.6161 | 1828.1984 | 1572.018 | 2352.24 | 2932.2223 | 2446.414 | 3174.6632 | 4276.4717 | 1770.2348 | 1876.3958 | 2173.6466 | 4481.7461 | 5602.1826 | 7468.2398 | 413.6917 | 557.3138 | 855 | 476.8946 | 642.4589 | 968.3495 | 540.0975 | 727.6041 | 1081.6989 | 2025 | 2089.9267 | 215.1846 | 239.3736
2026 | 1573.6604 | 2981.6723 | 2339.9937 | 1323.5145 | 2800 | 2302.9508 | 4686.9331 | 1898.9643 | 2102.1535 | 2538.2699 | 2538.2699 | 337.1532 | 496.9454 | 1276.6644 | 1537.6862 | 1147.4903 | 1553.5188 | 1828.1984 | 1510.2842 | 2292.3497 | 2932.2223 | 2217.3783 | 2996.0827 | 4276.4717 | 1719.8083 | 1839.2394 | 2173.6466 | 4327.33 | 5409.1625 | 7468.2398 | 386.9234 | 539.2022 | 855 | 446.0367 | 621.5804 | 966.3593 | 505.15 | 703.9585 | 1077.7186 | 2026 | 2022.0084 | 208.1916 | 231.5945
2027 | 1568.8462 | 2972.5074 | 2332.313 | 1323.1233 | 2800 | 2278.6911 | 4615.4664 | 1855.0249 | 2053.5126 | 2468.7344 | 2468.7344 | 320.5081 | 473.3659 | 1221.2182 | 1471.0501 | 1092.1301 | 1518.4214 | 1828.1984 | 1448.5504 | 2232.4594 | 2932.2223 | 1988.3427 | 2817.5021 | 4276.4717 | 1669.3818 | 1802.0831 | 2173.6466 | 4179.1069 | 5223.8837 | 7468.2398 | 360.1551 | 521.0907 | 855 | 415.1788 | 600.7018 | 964.3692 | 470.2025 | 680.3129 | 1073.7383 | 2027 | 1954.0902 | 201.1985 | 223.8153
2028 | 1563.7103 | 2961.1199 | 2323.3651 | 1323.1394 | 2800 | 2264.1508 | 4543.9998 | 1813.7619 | 2007.8344 | 2402.4789 | 2402.4789 | 305.9609 | 452.0794 | 1172.1772 | 1411.1335 | 1036.7699 | 1483.3241 | 1828.1984 | 1386.8165 | 2172.5691 | 2932.2223 | 1759.307 | 2638.9216 | 4276.4717 | 1618.9554 | 1764.9267 | 2173.6466 | 4036.8211 | 5046.0263 | 7468.2398 | 333.3868 | 502.9792 | 855 | 384.3209 | 579.8232 | 962.379 | 435.255 | 656.6672 | 1069.758 | 2028 | 1886.1719 | 194.2055 | 216.0362
2029 | 1556.6794 | 2946.8267 | 2312.4183 | 1323.5344 | 2800 | 2244.0188 | 4472.5332 | 1774.9242 | 1964.8411 | 2340.9667 | 2340.9667 | 292.6208 | 433.7767 | 1127.6608 | 1357.6338 | 981.4098 | 1448.2268 | 1828.1984 | 1325.0827 | 2112.6788 | 2932.2223 | 1530.2713 | 2460.341 | 4276.4717 | 1568.5289 | 1727.7704 | 2173.6466 | 3900.2274 | 4875.2842 | 7468.2398 | 306.6185 | 484.8676 | 855 | 353.463 | 558.9446 | 960.3889 | 400.3075 | 633.0216 | 1065.7777 | 2029 | 1818.2536 | 187.2124 | 208.257
2030 | 1550.9663 | 2933.6711 | 2301.9113 | 1323.5016 | 2800 | 2233.6649 | 4401.0666 | 1738.9512 | 1925.0189 | 2284.7736 | 2284.7736 | 281.2149 | 416.7589 | 1086.6891 | 1308.7009 | 926.0496 | 1413.1294 | 1828.1984 | 1263.3489 | 2052.7885 | 2932.2223 | 1301.2356 | 2281.7605 | 4276.4717 | 1518.1024 | 1690.614 | 2173.6466 | 3769.0909 | 4711.3636 | 7468.2398 | 279.8503 | 466.7561 | 855 | 322.6052 | 538.0661 | 958.3987 | 365.3601 | 609.376 | 1061.7974 | 2030 | 1750.3353 | 180.2194 | 200.4779
2031 | 1544.9686 | 2922.3551 | 2293.3486 | 1323.0563 | 2800 | 2212.0293 | 4365.3333 | 1703.7072 | 1886.0039 | 2238.2531 | 2238.2531 | 270.1208 | 401.7377 | 1049.8746 | 1264.1348 | 899.5641 | 1397.4628 | 1828.1984 | 1232.437 | 2033.4688 | 2932.2223 | 1269.6949 | 2238.4144 | 4276.4717 | 1497.8189 | 1672.3534 | 2173.6466 | 3643.1864 | 4553.983 | 7468.2398 | 274.3749 | 460.9216 | 855 | 316.2933 | 531.3402 | 957.7525 | 358.2117 | 601.7588 | 1060.5049 | 2031 | 1728.4562 | 177.9666 | 197.9719
2032 | 1539.4497 | 2910.5221 | 2283.6173 | 1323.7163 | 2800 | 2198.5572 | 4329.6 | 1669.1775 | 1847.7795 | 2192.6635 | 2192.6635 | 260.8345 | 387.8692 | 1016.2773 | 1223.7422 | 873.0786 | 1381.7961 | 1828.1984 | 1201.525 | 2014.1491 | 2932.2223 | 1238.1541 | 2195.0683 | 4276.4717 | 1477.4596 | 1654.0649 | 2173.6466 | 3522.2982 | 4402.8727 | 7468.2398 | 268.8996 | 455.0872 | 855 | 309.9815 | 524.6144 | 957.1062 | 351.0634 | 594.1416 | 1059.2125 | 2032 | 1706.577 | 175.7139 | 195.4659
2033 | 1535.1198 | 2901.8858 | 2276.4667 | 1323.2009 | 2800 | 2177.8836 | 4293.8667 | 1635.3477 | 1810.3299 | 2148.7246 | 2148.7246 | 251.7921 | 375.1038 | 985.0167 | 1185.8597 | 846.5931 | 1366.1294 | 1828.1984 | 1170.6131 | 1994.8294 | 2932.2223 | 1206.6134 | 2151.7222 | 4276.4717 | 1457.0245 | 1635.7486 | 2173.6466 | 3406.2193 | 4257.7741 | 7468.2398 | 263.4243 | 449.2527 | 855 | 303.6696 | 517.8886 | 956.46 | 343.915 | 586.5244 | 1057.92 | 2033 | 1684.6978 | 173.4611 | 192.96
2034 | 1530.4616 | 2891.1944 | 2268.1297 | 1323.7405 | 2800 | 2164.6195 | 4258.1334 | 1602.2035 | 1773.6392 | 2104.9288 | 2104.9288 | 243.7133 | 362.6686 | 955.9945 | 1151.1103 | 820.1076 | 1350.4627 | 1828.1984 | 1139.7011 | 1975.5097 | 2932.2223 | 1175.0727 | 2108.3761 | 4276.4717 | 1436.5137 | 1617.4045 | 2173.6466 | 3294.7514 | 4118.4392 | 7468.2398 | 257.9489 | 443.4183 | 855 | 297.3578 | 511.1627 | 955.8137 | 336.7667 | 578.9072 | 1056.6275 | 2034 | 1662.8186 | 171.2084 | 190.454
2035 | 1526.9133 | 2885.6738 | 2264.3633 | 1323.1349 | 2800 | 2144.4078 | 4222.4001 | 1569.731 | 1737.6922 | 2062.0099 | 2062.0099 | 235.8415 | 351.981 | 929.1157 | 1118.6439 | 793.6221 | 1334.796 | 1828.1984 | 1108.7892 | 1956.19 | 2932.2223 | 1143.532 | 2065.03 | 4276.4717 | 1415.927 | 1599.0325 | 2173.6466 | 3187.7044 | 3984.6305 | 7468.2398 | 252.4736 | 437.5838 | 855 | 291.046 | 504.4369 | 955.1675 | 329.6183 | 571.29 | 1055.335 | 2035 | 1640.9394 | 168.9557 | 187.948
2036 | 1523.012 | 2878.0448 | 2257.9213 | 1323.5366 | 2800 | 2131.3476 | 4186.6668 | 1537.9167 | 1702.4738 | 2020.6506 | 2020.6506 | 228.8718 | 341.5578 | 903.5885 | 1088.3657 | 773.5255 | 1319.1294 | 1828.1984 | 1077.8772 | 1936.8703 | 2932.2223 | 1111.9912 | 2021.6839 | 4276.4717 | 1395.2646 | 1580.6327 | 2173.6466 | 3084.8962 | 3856.1203 | 7468.2398 | 246.9983 | 431.7494 | 855 | 284.7341 | 497.7111 | 954.5213 | 322.47 | 563.6728 | 1054.0425 | 2036 | 1619.0602 | 166.7029 | 185.442
2037 | 1520.1464 | 2873.221 | 2254.4369 | 1323.5105 | 2800 | 2111.5849 | 4150.9335 | 1506.7472 | 1667.9691 | 1979.4217 | 1979.4217 | 222.0748 | 332.0808 | 880.0485 | 1059.4959 | 753.4289 | 1303.4627 | 1828.1984 | 1046.9653 | 1917.5506 | 2932.2223 | 1080.4505 | 1978.3378 | 4276.4717 | 1374.5265 | 1562.2051 | 2173.6466 | 2986.1521 | 3732.6902 | 7468.2398 | 241.5229 | 425.9149 | 855 | 278.4223 | 490.9853 | 953.875 | 315.3216 | 556.0556 | 1052.75 | 2037 | 1597.181 | 164.4502 | 182.9361
2038 | 1516.9059 | 2867.668 | 2249.6943 | 1323.0715 | 2800 | 2098.7246 | 4115.2002 | 1476.2093 | 1634.1637 | 1939.6944 | 1939.6944 | 216.1219 | 323.5075 | 857.734 | 1032.6577 | 733.3324 | 1287.796 | 1828.1984 | 1016.0534 | 1898.2309 | 2932.2223 | 1048.9098 | 1934.9917 | 4276.4717 | 1353.7125 | 1543.7496 | 2173.6466 | 2891.3048 | 3614.131 | 7468.2398 | 236.0476 | 420.0805 | 855 | 272.1104 | 484.2594 | 953.2288 | 308.1733 | 548.4384 | 1051.4576 | 2038 | 1575.3018 | 162.1974 | 180.4301
2039 | 1515.2951 | 2864.0669 | 2247.0685 | 1323.5611 | 2800 | 2079.3983 | 4079.4669 | 1446.2905 | 1601.0435 | 1900.0898 | 1900.0898 | 210.3102 | 315.1336 | 836.5968 | 1007.7641 | 713.2358 | 1272.1293 | 1828.1984 | 985.1414 | 1878.9112 | 2932.2223 | 1017.369 | 1891.6456 | 4276.4717 | 1332.8228 | 1525.2663 | 2173.6466 | 2800.1938 | 3500.2423 | 7468.2398 | 230.5723 | 414.246 | 855 | 265.7986 | 477.5336 | 952.5825 | 301.0249 | 540.8212 | 1050.1651 | 2039 | 1553.4226 | 159.9447 | 177.9241
2040 | 1510.6601 | 2855.7863 | 2241.2252 | 1323.6198 | 2800 | 2066.734 | 4043.7336 | 1416.978 | 1568.5946 | 1861.2792 | 1861.2792 | 205.2882 | 306.9547 | 816.5906 | 983.428 | 693.1392 | 1256.4626 | 1828.1984 | 954.2295 | 1859.5915 | 2932.2223 | 985.8283 | 1848.2995 | 4276.4717 | 1311.8573 | 1506.7552 | 2173.6466 | 2712.6653 | 3390.8317 | 7468.2398 | 225.0969 | 408.4116 | 855 | 259.4868 | 470.8078 | 951.9363 | 293.8766 | 533.204 | 1048.8726 | 2040 | 1531.5434 | 157.6919 | 175.4181
2041 | 1510.8368 | 2855.8657 | 2241.288 | 1323.2626 | 2800 | 2047.8319 | 4011.5736 | 1388.2595 | 1536.8033 | 1823.8873 | 1823.8873 | 200.3779 | 299.6066 | 797.6706 | 960.9178 | 680.9496 | 1242.8793 | 1828.1984 | 945.8448 | 1837.8554 | 2932.2223 | 970.7421 | 1829.6989 | 4276.4717 | 1290.816 | 1488.2162 | 2173.6466 | 2628.572 | 3285.715 | 7468.2398 | 219.6216 | 402.5771 | 855 | 253.1749 | 464.082 | 951.2901 | 286.7282 | 525.5868 | 1047.5801 | 2041 | 1509.6642 | 155.4392 | 172.9122
2042 | 1511.1638 | 2856.3071 | 2241.2767 | 1323.133 | 2800 | 2035.3599 | 3979.4136 | 1360.1232 | 1505.6563 | 1786.6069 | 1786.6069 | 195.5772 | 292.4225 | 779.7932 | 938.8962 | 668.7599 | 1229.2959 | 1828.1984 | 937.46 | 1816.1194 | 2932.2223 | 955.656 | 1811.0983 | 4276.4717 | 1269.6989 | 1469.6494 | 2173.6466 | 2547.7724 | 3184.7155 | 7468.2398 | 214.1463 | 396.7427 | 855 | 246.8631 | 457.3561 | 950.6438 | 279.5799 | 517.9696 | 1046.2876 | 2042 | 1487.785 | 153.1865 | 170.4062
2043 | 1511.0069 | 2855.8401 | 2241.1828 | 1323.2121 | 2800 | 2016.8703 | 3947.2536 | 1332.557 | 1475.1406 | 1750.6924 | 1750.6924 | 190.8835 | 286.0164 | 762.2987 | 917.9707 | 656.5702 | 1215.7125 | 1828.1984 | 929.0753 | 1794.3833 | 2932.2223 | 940.5698 | 1792.4977 | 4276.4717 | 1248.5061 | 1451.0547 | 2173.6466 | 2470.1313 | 3087.6641 | 7468.2398 | 208.6709 | 390.9082 | 855 | 240.5512 | 450.6303 | 949.9976 | 272.4315 | 510.3524 | 1044.9951 | 2043 | 1465.9059 | 150.9337 | 167.9002
2044 | 1510.9899 | 2856.3171 | 2240.9983 | 1323.4815 | 2800 | 2004.5868 | 3915.0937 | 1305.5496 | 1445.2434 | 1715.4893 | 1715.4893 | 186.2947 | 279.7455 | 745.7858 | 898.0984 | 644.3806 | 1202.1291 | 1828.1984 | 920.6906 | 1772.6472 | 2932.2223 | 925.4837 | 1773.8971 | 4276.4717 | 1227.2374 | 1432.4322 | 2173.6466 | 2395.5187 | 2994.3983 | 7468.2398 | 203.1956 | 385.0738 | 855 | 234.2394 | 443.9045 | 949.3513 | 265.2832 | 502.7352 | 1043.7026 | 2044 | 1444.0267 | 148.681 | 165.3942
2045 | 1511.0972 | 2855.8843 | 2241.3118 | 1323.3277 | 2800 | 1986.4981 | 3882.9337 | 1279.0895 | 1415.9521 | 1680.3878 | 1680.3878 | 182.4046 | 273.6069 | 729.6185 | 879.238 | 632.1909 | 1188.5457 | 1828.1984 | 879.8006 | 1750.9111 | 2932.2223 | 910.3975 | 1755.2965 | 4276.4717 | 1205.893 | 1413.7819 | 2173.6466 | 2323.8102 | 2904.7627 | 7468.2398 | 197.7203 | 379.2393 | 855 | 227.9276 | 437.1787 | 948.7051 | 258.1348 | 495.118 | 1042.4102 | 2045 | 1422.1475 | 146.4282 | 162.8883
2046 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 622.5102 | 1174.9624 | 1828.1984 | 877.9169 | 1729.1751 | 2932.2223 | 906.518 | 1750.9172 | 4276.4717 | 1184.4729 | 1395.1038 | 2173.6466 | 2254.8866 | 2818.6082 | 7468.2398 | 192.245 | 373.4049 | 855 | 221.6157 | 430.4528 | 948.0588 | 250.9865 | 487.5008 | 1041.1177 | 2046 | 1400.2683 | 144.1755 | 160.3823
2047 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 612.8296 | 1161.379 | 1828.1984 | 876.0333 | 1707.439 | 2932.2223 | 902.6385 | 1746.5379 | 4276.4717 | 1162.9769 | 1376.3978 | 2173.6466 | 2188.6335 | 2735.7919 | 7468.2398 | 186.7696 | 367.5704 | 855 | 215.3039 | 423.727 | 947.4126 | 243.8381 | 479.8836 | 1039.8252 | 2047 | 1378.3891 | 141.9228 | 157.8763
2048 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 603.1489 | 1147.7956 | 1828.1984 | 874.1496 | 1685.7029 | 2932.2223 | 898.759 | 1742.1586 | 4276.4717 | 1141.4052 | 1357.6639 | 2173.6466 | 2124.9413 | 2656.1767 | 7468.2398 | 181.2943 | 361.736 | 855 | 208.992 | 417.0012 | 946.7664 | 236.6898 | 472.2664 | 1038.5327 | 2048 | 1356.5099 | 139.67 | 155.3704
2049 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 593.4682 | 1134.2122 | 1828.1984 | 872.266 | 1663.9668 | 2932.2223 | 894.8795 | 1737.7793 | 4276.4717 | 1119.7577 | 1338.9023 | 2173.6466 | 2063.705 | 2579.6313 | 7468.2398 | 175.819 | 355.9015 | 855 | 202.6802 | 410.2754 | 946.1201 | 229.5414 | 464.6492 | 1037.2402 | 2049 | 1334.6307 | 137.4173 | 152.8644
2050 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 583.7875 | 1120.6288 | 1828.1984 | 870.3823 | 1642.2308 | 2932.2223 | 891 | 1733.4 | 4276.4717 | 1098.0344 | 1320.1128 | 2173.6466 | 2004.824 | 2506.03 | 7468.2398 | 170.3436 | 350.0671 | 855 | 196.3684 | 403.5495 | 945.4739 | 222.3931 | 457.032 | 1035.9477 | 2050 | 1312.7515 | 135.1645 | 150.3584
fixed operation and maintenance (base-year $/kW-year)
technology | CC_152 | IC_MCBH | IC_Schofield | IC_Barge | Lake_Wilson | OnshoreWind | OffshoreWind | CentralFixedPV | CentralTrackingPV | FlatDistPV | SlopedDistPV | Battery_Conting | Battery_Reg | Battery_4 | Battery_6 | CentralTrackingPV | CentralTrackingPV | CentralTrackingPV | FlatDistPV | FlatDistPV | FlatDistPV | SlopedDistPV | SlopedDistPV | SlopedDistPV | OnshoreWind | OnshoreWind | OnshoreWind | OffshoreWind | OffshoreWind | OffshoreWind | Battery_Bulk | Battery_Bulk | Battery_Bulk | Battery_Conting | Battery_Conting | Battery_Conting | Battery_Reg | Battery_Reg | Battery_Reg
tech_scen_id | all | all | all | all | all | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high
2017 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 19.8672 | 19.8672 | 19.8672 | 17.9354 | 17.9354 | 17.9354 | 23.4278 | 23.4278 | 23.4278 | 43.56 | 43.56 | 43.56 | 87.4043 | 87.4043 | 87.4043 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094
2018 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 13.8029 | 13.8029 | 13.8029 | 17.1023 | 17.1023 | 17.1023 | 21.4755 | 21.4755 | 21.4755 | 42.8538 | 43.2054 | 43.56 | 67.9543 | 84.9429 | 87.4043 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094 | 37.1094
2019 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 11.3831 | 12.9637 | 13.8029 | 13.1465 | 16.992 | 17.1023 | 18.7685 | 20.6026 | 21.4755 | 42.1477 | 42.8508 | 43.56 | 66.0406 | 82.5508 | 87.4043 | 33.0774 | 34.6055 | 37.1094 | 33.0774 | 34.6055 | 37.1094 | 33.0774 | 34.6055 | 37.1094
2020 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 10.6802 | 12.72 | 13.8029 | 12.3101 | 16.009 | 17.1023 | 17.7363 | 20.0867 | 21.4755 | 41.4415 | 42.4962 | 43.56 | 64.1809 | 80.2261 | 87.4043 | 29.0454 | 32.1016 | 35.9649 | 29.0454 | 32.1016 | 35.9649 | 29.0454 | 32.1016 | 35.9649
2021 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 10.2806 | 12.48 | 13.8029 | 11.0761 | 15.7822 | 17.1023 | 16.6052 | 19.2049 | 21.4755 | 40.7354 | 42.1415 | 43.56 | 62.3735 | 77.9669 | 87.4043 | 26.8274 | 30.5191 | 35.6539 | 26.8274 | 30.5191 | 35.6539 | 26.8274 | 30.5191 | 35.6539
2022 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 9.881 | 12.2267 | 13.8029 | 10.7002 | 15.4175 | 17.1023 | 15.4742 | 18.323 | 21.4755 | 40.0292 | 41.7869 | 43.56 | 60.617 | 75.7712 | 87.4043 | 24.6094 | 28.9366 | 35.343 | 24.6094 | 28.9366 | 35.343 | 24.6094 | 28.9366 | 35.343
2023 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 9.4814 | 11.9733 | 13.8029 | 10.3243 | 15.0528 | 17.1023 | 14.3431 | 17.4411 | 21.4755 | 39.3231 | 41.4323 | 43.56 | 58.91 | 73.6374 | 87.4043 | 22.3914 | 27.354 | 35.032 | 22.3914 | 27.354 | 35.032 | 22.3914 | 27.354 | 35.032
2024 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 9.0818 | 11.72 | 13.8029 | 9.9484 | 14.6881 | 17.1023 | 13.2121 | 16.5592 | 21.4755 | 38.6169 | 41.0777 | 43.56 | 57.251 | 71.5637 | 87.4043 | 20.1734 | 25.7715 | 34.721 | 20.1734 | 25.7715 | 34.721 | 20.1734 | 25.7715 | 34.721
2025 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 8.6822 | 11.4667 | 13.8029 | 9.5725 | 14.3234 | 17.1023 | 12.0811 | 15.6773 | 21.4755 | 37.9108 | 40.7231 | 43.56 | 55.6388 | 69.5484 | 87.4043 | 17.9554 | 24.189 | 34.4101 | 17.9554 | 24.189 | 34.4101 | 17.9554 | 24.189 | 34.4101
2026 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 8.2826 | 11.2133 | 13.8029 | 9.1965 | 13.9588 | 17.1023 | 10.95 | 14.7955 | 21.4755 | 37.2046 | 40.3685 | 43.56 | 54.0719 | 67.5899 | 87.4043 | 16.7936 | 23.4029 | 34.0991 | 16.7936 | 23.4029 | 34.0991 | 16.7936 | 23.4029 | 34.0991
2027 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 7.883 | 10.96 | 13.8029 | 8.8206 | 13.5941 | 17.1023 | 9.819 | 13.9136 | 21.4755 | 36.4985 | 40.0138 | 43.56 | 52.5492 | 65.6865 | 87.4043 | 15.6317 | 22.6168 | 33.7882 | 15.6317 | 22.6168 | 33.7882 | 15.6317 | 22.6168 | 33.7882
2028 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 7.4834 | 10.7067 | 13.8029 | 8.4447 | 13.2294 | 17.1023 | 8.6879 | 13.0317 | 21.4755 | 35.7923 | 39.6592 | 43.56 | 51.0694 | 63.8367 | 87.4043 | 14.4699 | 21.8307 | 33.4772 | 14.4699 | 21.8307 | 33.4772 | 14.4699 | 21.8307 | 33.4772
2029 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 7.0838 | 10.4533 | 13.8029 | 8.0688 | 12.8647 | 17.1023 | 7.5569 | 12.1498 | 21.4755 | 35.0862 | 39.3046 | 43.56 | 49.6312 | 62.039 | 87.4043 | 13.3081 | 21.0446 | 33.1662 | 13.3081 | 21.0446 | 33.1662 | 13.3081 | 21.0446 | 33.1662
2030 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 6.6842 | 10.2 | 13.8029 | 7.6929 | 12.5 | 17.1023 | 6.4259 | 11.268 | 21.4755 | 34.38 | 38.95 | 43.56 | 48.2335 | 60.2919 | 87.4043 | 12.1463 | 20.2585 | 32.8553 | 12.1463 | 20.2585 | 32.8553 | 12.1463 | 20.2585 | 32.8553
2031 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 6.4931 | 10.0869 | 13.8029 | 7.5047 | 12.3824 | 17.1023 | 6.2701 | 11.0539 | 21.4755 | 33.8643 | 38.6579 | 43.56 | 46.8752 | 58.5941 | 87.4043 | 11.9086 | 20.0053 | 32.7543 | 11.9086 | 20.0053 | 32.7543 | 11.9086 | 20.0053 | 32.7543
2032 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 6.3019 | 9.9738 | 13.8029 | 7.3164 | 12.2647 | 17.1023 | 6.1143 | 10.8398 | 21.4755 | 33.3486 | 38.3658 | 43.56 | 45.5552 | 56.944 | 87.4043 | 11.671 | 19.752 | 32.6533 | 11.671 | 19.752 | 32.6533 | 11.671 | 19.752 | 32.6533
2033 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 6.1107 | 9.8608 | 13.8029 | 7.1282 | 12.1471 | 17.1023 | 5.9586 | 10.6258 | 21.4755 | 32.8329 | 38.0736 | 43.56 | 44.2723 | 55.3404 | 87.4043 | 11.4333 | 19.4988 | 32.5523 | 11.4333 | 19.4988 | 32.5523 | 11.4333 | 19.4988 | 32.5523
2034 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 5.9196 | 9.7477 | 13.8029 | 6.94 | 12.0294 | 17.1023 | 5.8028 | 10.4117 | 21.4755 | 32.3172 | 37.7815 | 43.56 | 43.0256 | 53.782 | 87.4043 | 11.1957 | 19.2456 | 32.4514 | 11.1957 | 19.2456 | 32.4514 | 11.1957 | 19.2456 | 32.4514
2035 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 5.7284 | 9.6346 | 13.8029 | 6.7517 | 11.9118 | 17.1023 | 5.6471 | 10.1977 | 21.4755 | 31.8015 | 37.4894 | 43.56 | 41.8139 | 52.2674 | 87.4043 | 10.9581 | 18.9924 | 32.3504 | 10.9581 | 18.9924 | 32.3504 | 10.9581 | 18.9924 | 32.3504
2036 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 5.5833 | 9.5215 | 13.8029 | 6.5635 | 11.7941 | 17.1023 | 5.4913 | 9.9836 | 21.4755 | 31.2858 | 37.1973 | 43.56 | 40.6364 | 50.7955 | 87.4043 | 10.7204 | 18.7391 | 32.2494 | 10.7204 | 18.7391 | 32.2494 | 10.7204 | 18.7391 | 32.2494
2037 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 5.4383 | 9.4084 | 13.8029 | 6.3753 | 11.6765 | 17.1023 | 5.3356 | 9.7696 | 21.4755 | 30.7701 | 36.9051 | 43.56 | 39.492 | 49.3651 | 87.4043 | 10.4828 | 18.4859 | 32.1484 | 10.4828 | 18.4859 | 32.1484 | 10.4828 | 18.4859 | 32.1484
2038 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 5.2932 | 9.2953 | 13.8029 | 6.187 | 11.5589 | 17.1023 | 5.1798 | 9.5555 | 21.4755 | 30.2544 | 36.613 | 43.56 | 38.3799 | 47.9749 | 87.4043 | 10.2451 | 18.2327 | 32.0475 | 10.2451 | 18.2327 | 32.0475 | 10.2451 | 18.2327 | 32.0475
2039 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 5.1482 | 9.1823 | 13.8029 | 5.9988 | 11.4412 | 17.1023 | 5.024 | 9.3415 | 21.4755 | 29.7387 | 36.3209 | 43.56 | 37.2991 | 46.6239 | 87.4043 | 10.0075 | 17.9794 | 31.9465 | 10.0075 | 17.9794 | 31.9465 | 10.0075 | 17.9794 | 31.9465
2040 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 5.0031 | 9.0692 | 13.8029 | 5.8106 | 11.3236 | 17.1023 | 4.8683 | 9.1274 | 21.4755 | 29.223 | 36.0288 | 43.56 | 36.2487 | 45.3109 | 87.4043 | 9.7698 | 17.7262 | 31.8455 | 9.7698 | 17.7262 | 31.8455 | 9.7698 | 17.7262 | 31.8455
2041 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.9151 | 8.9711 | 13.8029 | 5.7595 | 11.1912 | 17.1023 | 4.7938 | 9.0356 | 21.4755 | 28.7073 | 35.7366 | 43.56 | 35.2279 | 44.0349 | 87.4043 | 9.5322 | 17.473 | 31.7445 | 9.5322 | 17.473 | 31.7445 | 9.5322 | 17.473 | 31.7445
2042 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.8271 | 8.8731 | 13.8029 | 5.7085 | 11.0589 | 17.1023 | 4.7193 | 8.9437 | 21.4755 | 28.1916 | 35.4445 | 43.56 | 34.2359 | 42.7948 | 87.4043 | 9.2945 | 17.2197 | 31.6436 | 9.2945 | 17.2197 | 31.6436 | 9.2945 | 17.2197 | 31.6436
2043 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.7391 | 8.775 | 13.8029 | 5.6574 | 10.9265 | 17.1023 | 4.6448 | 8.8518 | 21.4755 | 27.6759 | 35.1524 | 43.56 | 33.2718 | 41.5897 | 87.4043 | 9.0569 | 16.9665 | 31.5426 | 9.0569 | 16.9665 | 31.5426 | 9.0569 | 16.9665 | 31.5426
2044 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.6512 | 8.677 | 13.8029 | 5.6063 | 10.7941 | 17.1023 | 4.5703 | 8.76 | 21.4755 | 27.1602 | 34.8603 | 43.56 | 32.3348 | 40.4185 | 87.4043 | 8.8193 | 16.7133 | 31.4416 | 8.8193 | 16.7133 | 31.4416 | 8.8193 | 16.7133 | 31.4416
2045 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.5632 | 8.5789 | 13.8029 | 5.3574 | 10.6618 | 17.1023 | 4.4958 | 8.6681 | 21.4755 | 26.6445 | 34.5681 | 43.56 | 31.4242 | 39.2803 | 87.4043 | 8.5816 | 16.46 | 31.3406 | 8.5816 | 16.46 | 31.3406 | 8.5816 | 16.46 | 31.3406
2046 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.4933 | 8.4809 | 13.8029 | 5.3459 | 10.5294 | 17.1023 | 4.4766 | 8.6465 | 21.4755 | 26.1288 | 34.276 | 43.56 | 30.5393 | 38.1741 | 87.4043 | 8.344 | 16.2068 | 31.2397 | 8.344 | 16.2068 | 31.2397 | 8.344 | 16.2068 | 31.2397
2047 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.4234 | 8.3829 | 13.8029 | 5.3344 | 10.3971 | 17.1023 | 4.4575 | 8.6249 | 21.4755 | 25.6131 | 33.9839 | 43.56 | 29.6793 | 37.0991 | 87.4043 | 8.1063 | 15.9536 | 31.1387 | 8.1063 | 15.9536 | 31.1387 | 8.1063 | 15.9536 | 31.1387
2048 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.3535 | 8.2848 | 13.8029 | 5.3229 | 10.2647 | 17.1023 | 4.4383 | 8.6033 | 21.4755 | 25.0974 | 33.6917 | 43.56 | 28.8435 | 36.0543 | 87.4043 | 7.8687 | 15.7003 | 31.0377 | 7.8687 | 15.7003 | 31.0377 | 7.8687 | 15.7003 | 31.0377
2049 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.2837 | 8.1868 | 13.8029 | 5.3115 | 10.1324 | 17.1023 | 4.4192 | 8.5816 | 21.4755 | 24.5817 | 33.3996 | 43.56 | 28.0312 | 35.039 | 87.4043 | 7.631 | 15.4471 | 30.9367 | 7.631 | 15.4471 | 30.9367 | 7.631 | 15.4471 | 30.9367
2050 | 17.29 | 34.46 | 34.46 | 34.46 | 42 | 27.4 | 96.71 | 22.97 | 27.4 | 0 | 0 | 5.42 | 7.61 | 19.47 | 27.49 | 4.2138 | 8.0887 | 13.8029 | 5.3 | 10 | 17.1023 | 4.4 | 8.56 | 21.4755 | 24.066 | 33.1075 | 43.56 | 27.2418 | 34.0523 | 87.4043 | 7.3934 | 15.1939 | 30.8358 | 7.3934 | 15.1939 | 30.8358 | 7.3934 | 15.1939 | 30.8358
capital cost for storage energy (base-year $ per kWh) (note: per-kWh cost for fixed-size technologies is generally included in per-kW cost)
technology | Battery_Conting | Battery_Reg | Battery_4 | Battery_6 | Battery_Bulk | Battery_Bulk | Battery_Bulk | Battery_Conting | Battery_Conting | Battery_Conting | Battery_Reg | Battery_Reg | Battery_Reg
tech_scen_id | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | PSIP_2016_12 | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high | ATB_2019_low | ATB_2019_mid | ATB_2019_high
2017 | 0 | 0 | 0 | 0 | 261.25 | 261.25 | 261.25 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 0 | 0 | 0 | 0 | 261.25 | 261.25 | 261.25 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 0 | 0 | 0 | 0 | 232.865 | 243.6227 | 261.25 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 0 | 0 | 0 | 0 | 204.48 | 225.9954 | 246.6005 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 188.8651 | 214.8544 | 242.6202 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 0 | 0 | 0 | 0 | 173.2503 | 203.7134 | 238.6399 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 0 | 0 | 0 | 0 | 157.6355 | 192.5724 | 234.6596 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 0 | 0 | 0 | 0 | 142.0206 | 181.4313 | 230.6792 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | 0 | 0 | 0 | 126.4058 | 170.2903 | 226.6989 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 0 | 0 | 0 | 0 | 118.2266 | 164.7562 | 222.7186 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | 0 | 0 | 0 | 110.0474 | 159.2222 | 218.7383 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 | 0 | 0 | 0 | 101.8682 | 153.6881 | 214.758 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 | 0 | 0 | 0 | 93.689 | 148.154 | 210.7777 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0 | 0 | 0 | 0 | 85.5098 | 142.6199 | 206.7974 | 0 | 0 | 0 | 0 | 0 | 0
2031 | 0 | 0 | 0 | 0 | 83.8368 | 140.8372 | 205.5049 | 0 | 0 | 0 | 0 | 0 | 0
2032 | 0 | 0 | 0 | 0 | 82.1638 | 139.0544 | 204.2125 | 0 | 0 | 0 | 0 | 0 | 0
2033 | 0 | 0 | 0 | 0 | 80.4907 | 137.2717 | 202.92 | 0 | 0 | 0 | 0 | 0 | 0
2034 | 0 | 0 | 0 | 0 | 78.8177 | 135.4889 | 201.6275 | 0 | 0 | 0 | 0 | 0 | 0
2035 | 0 | 0 | 0 | 0 | 77.1447 | 133.7062 | 200.335 | 0 | 0 | 0 | 0 | 0 | 0
2036 | 0 | 0 | 0 | 0 | 75.4717 | 131.9234 | 199.0425 | 0 | 0 | 0 | 0 | 0 | 0
2037 | 0 | 0 | 0 | 0 | 73.7987 | 130.1407 | 197.75 | 0 | 0 | 0 | 0 | 0 | 0
2038 | 0 | 0 | 0 | 0 | 72.1257 | 128.3579 | 196.4576 | 0 | 0 | 0 | 0 | 0 | 0
2039 | 0 | 0 | 0 | 0 | 70.4526 | 126.5752 | 195.1651 | 0 | 0 | 0 | 0 | 0 | 0
2040 | 0 | 0 | 0 | 0 | 68.7796 | 124.7924 | 193.8726 | 0 | 0 | 0 | 0 | 0 | 0
2041 | 0 | 0 | 0 | 0 | 67.1066 | 123.0097 | 192.5801 | 0 | 0 | 0 | 0 | 0 | 0
2042 | 0 | 0 | 0 | 0 | 65.4336 | 121.2269 | 191.2876 | 0 | 0 | 0 | 0 | 0 | 0
2043 | 0 | 0 | 0 | 0 | 63.7606 | 119.4442 | 189.9951 | 0 | 0 | 0 | 0 | 0 | 0
2044 | 0 | 0 | 0 | 0 | 62.0876 | 117.6614 | 188.7026 | 0 | 0 | 0 | 0 | 0 | 0
2045 | 0 | 0 | 0 | 0 | 60.4145 | 115.8787 | 187.4102 | 0 | 0 | 0 | 0 | 0 | 0
2046 | 0 | 0 | 0 | 0 | 58.7415 | 114.0959 | 186.1177 | 0 | 0 | 0 | 0 | 0 | 0
2047 | 0 | 0 | 0 | 0 | 57.0685 | 112.3132 | 184.8252 | 0 | 0 | 0 | 0 | 0 | 0
2048 | 0 | 0 | 0 | 0 | 55.3955 | 110.5304 | 183.5327 | 0 | 0 | 0 | 0 | 0 | 0
2049 | 0 | 0 | 0 | 0 | 53.7225 | 108.7477 | 182.2402 | 0 | 0 | 0 | 0 | 0 | 0
2050 | 0 | 0 | 0 | 0 | 52.0494 | 106.9649 | 180.9477 | 0 | 0 | 0 | 0 | 0 | 0

## PSIP costs
copied from "PSIP 2016 New Generation Assumptions REVISED 16-June-16.xlsx" with state tax credit omitted from renewables
these are nominal project costs; earlier versions were shown in PSIP 2016-04-01 J-67 - J-70 and Appendix F (main difference is more expensive offshore wind now); may also be in 2016-09-07 workplan
short names assigned manually below
inflation rate | 1.8% | [15 empty] | These columns are from storage page |  |  |  | From John Wehrheim
base year | 2016
Technology ID | OnshoreWind | OffshoreWind | MauiOahuWind200 | MauiOahuWind400 | CentralFixedPV | FlatDistPV | SolarCSPStorage | CC_383 | CC_152 | CT_100 | Biomass | IC_MCBH | IC_Schofield | IC_Barge | SlopedDistPV | CentralTrackingPV | Battery_Conting | Battery_Reg | Battery_4 | Battery_6 | Lake_Wilson
Technology | On-Shore Wind | Offshore Wind Floating Platform | On Shore Wind + Cable | On Shore Wind + Cable | Utility Scale Solar PV | DG Solar PV | Solar CSP w 10 hrs storage | Combined Cycle Gas | Combined Cycle Gas | Simple Cycle Gas | Biomass | Internal Combustion | Internal Combustion | Internal Combustion | DG Solar PV | Utility Scale Tracking Solar PV | Batteries | Batteries | Batteries | Batteries | Pumped Hydro
Primary Data Source | IHS Energy RS Means | NREL | IHS Energy RSMeans Vendor Quotes | IHS Energy RSMeans Vendor Quotes | IHS Energy RSMeans | IHS Energy RSMeans | NREL | NextEra | NextEra | Gas Turbine World RSMeans | NREL | HECO | HECO Schofield Application | HECO | IHS Energy RSMeans | IHS Energy RS Means (adjusted)
Size (MW) | 30 | 400 | 200 | 400 | 20 | DG-PV | 100 | 383 (3 x 1) | 152 (1 x 1) | 100 | 20 | 27 (3 x 9 MW) | 54 (6 x 9 MW) | 100 (6 x 16.8 MW) Power Barge | DG-PV | 30 | 100 | 100 | 100 | 100 | 150
Fuel | NA | NA | NA | NA | NA | NA | NA | Gas / Oil | Gas / Oil | Gas / Oil | Biomass | Gas / Oil | Gas/Oil | Gas / Oil | NA | NA | NA | NA | NA | NA | NA
Hawaii Specific Nominal (As-Spent) Overnight Capital Cost $/KWAC (AFUDC NOT included)
Island | Oahu | Oahu | Maui --> Oahu | Maui --> Oahu | Oahu | Oahu | Oahu | Oahu | Oahu | Oahu | Oahu / Maui / Hawaii | Oahu / Maui / Hawaii | Oahu/ Maui/ Hawaii | Oahu | Oahu | Oahu | Oahu | Oahu | Oahu | Oahu | Oahu
Install Year | [14 empty] | 0
2016 | 2464.704 | 6402.1317 | N/A | N/A | 2792.5543 | 3945 | 12304 | 1758 | 1660 | 1237 | 6296 | 3177 | 2493 | 1323 | 3945 | 3091.3576 | 753 | 1083 | 2640 | 3180 | 2800
2017 | 2503.5973 | 6317.2993 | N/A | N/A | 2626.6215 | 3716 | 12525 | 1783 | 1683 | 1253 | 6092 | 3219 | 2526 | 1347 | 3716 | 2907.67 | 692 | 999 | 2458 | 2960 | 2850.4
2018 | 2442.6907 | 6227.3386 | N/A | N/A | 2547.4511 | 3573 | 11681 | 1797 | 1697 | 1261 | 6178 | 3238 | 2541 | 1371 | 3573 | 2820.0283 | 631 | 914 | 2261 | 2723 | 2901.7072
2019 | 2427.5813 | 6132.0926 | N/A | N/A | 2483.5441 | 3457 | 10781 | 1822 | 1720 | 1277 | 6269 | 3280 | 2574 | 1396 | 3457 | 2749.2833 | 581 | 843 | 2095 | 2523 | 2953.9379
2020 | 2480.3014 | 6031.4 | 5097.2649 | 4572.2896 | 2431.5565 | 3360 | 9848 | 1845 | 1742 | 1292 | 6354 | 3319 | 2604 | 1421 | 3360 | 2691.7331 | 539 | 782 | 1948 | 2346 | 3007.1088
2021 | 2520.4131 | 5879.5173 | 5207.2307 | 4671.7559 | 2392.2978 | 3285 | 8874 | 1870 | 1766 | 1309 | 6446 | 3362 | 2638 | 1447 | 3285 | 2648.2737 | 506 | 737 | 1846 | 2223 | 3061.2368
2022 | 2586.2085 | 5720.2127 | 5324.2257 | 4778.0413 | 2357.4915 | 3218 | 7867 | 1896 | 1790 | 1326 | 6541 | 3406 | 2672 | 1473 | 3218 | 2609.7431 | 478 | 698 | 1760 | 2120 | 3116.339
2023 | 2643.9703 | 5553.2682 | 5456.1223 | 4899.0143 | 2328.0931 | 3160 | 7813 | 1921 | 1813 | 1342 | 6633 | 3448 | 2705 | 1499 | 3160 | 2577.1991 | 455 | 666 | 1687 | 2032 | 3172.4331
2024 | 2690.5278 | 5570.797 | 5559.9164 | 4991.6662 | 2303.8504 | 3111 | 7756 | 1944 | 1836 | 1358 | 6725 | 3487 | 2736 | 1526 | 3111 | 2550.3624 | 435 | 638 | 1625 | 1957 | 3229.5369
2025 | 2721.626 | 5587.1575 | 5664.176 | 5084.5608 | 2284.3509 | 3068 | 7694 | 1969 | 1859 | 1373 | 6826 | 3527 | 2768 | 1554 | 3068 | 2528.7765 | 418 | 614 | 1572 | 1893 | 3287.6686
2026 | 2752.7226 | 5602.3022 | 5757.6863 | 5166.4788 | 2269.8365 | 3034 | 7627 | 1992 | 1881 | 1388 | 6918 | 3564 | 2797 | 1582 | 3034 | 2512.709 | 403 | 594 | 1526 | 1838 | 3346.8466
2027 | 2772.752 | 5616.1818 | 5850.968 | 5247.9363 | 2257.2273 | 3004 | 7555 | 2021 | 1909 | 1408 | 7019 | 3617 | 2838 | 1610 | 3004 | 2498.7507 | 390 | 576 | 1486 | 1790 | 3407.0899
2028 | 2804.65 | 5628.7459 | 5947.9606 | 5332.8683 | 2246.7441 | 2976 | 7478 | 2051 | 1937 | 1428 | 7121 | 3668 | 2878 | 1639 | 2976 | 2487.1457 | 379 | 560 | 1452 | 1748 | 3468.4175
2029 | 2829.747 | 5639.9427 | 6049.11 | 5421.7158 | 2238.2105 | 2952 | 7396 | 2079 | 1963 | 1447 | 7222 | 3716 | 2916 | 1669 | 2952 | 2477.699 | 369 | 547 | 1422 | 1712 | 3530.849
2030 | 2867.3909 | 5649.7188 | 6153.9239 | 5513.9819 | 2232.3191 | 2933 | 7309 | 2108 | 1991 | 1466 | 7323 | 3766 | 2955 | 1699 | 2933 | 2471.1773 | 361 | 535 | 1395 | 1680 | 3594.4043
2031 | 2890.7301 | 5704.7167 | 6256.9423 | 5604.2015 | 2226.4432 | 2925 | 7216 | 2139 | 2019 | 1487 | 7425 | 3819 | 2997 | 1729 | 2925 | 2464.6727 | 353 | 525 | 1372 | 1652 | 3659.1036
2032 | 2924.8408 | 5759.8639 | 6361.7845 | 5695.9888 | 2220.5828 | 2917 | 7117 | 2169 | 2048 | 1507 | 7528 | 3872 | 3038 | 1761 | 2917 | 2458.1852 | 347 | 516 | 1352 | 1628 | 3724.9674
2033 | 2949.4897 | 5815.1482 | 6468.4839 | 5789.3724 | 2214.7378 | 2910 | 7245 | 2202 | 2079 | 1530 | 7638 | 3930 | 3083 | 1792 | 2910 | 2451.7148 | 341 | 508 | 1334 | 1606 | 3792.0168
2034 | 2984.2937 | 5870.5564 | 6577.0751 | 5884.3813 | 2208.9082 | 2902 | 7375 | 2234 | 2110 | 1552 | 7743 | 3986 | 3127 | 1825 | 2902 | 2445.2614 | 336 | 500 | 1318 | 1587 | 3860.2731
2035 | 3009.6443 | 5926.0753 | 6687.5928 | 5981.0451 | 2203.094 | 2894 | 7508 | 2270 | 2143 | 1577 | 7850 | 4050 | 3178 | 1857 | 2894 | 2438.825 | 331 | 494 | 1304 | 1570 | 3929.7581
2036 | 3045.1581 | 5981.6908 | 6800.0729 | 6079.3942 | 2197.295 | 2887 | 7643 | 2304 | 2176 | 1601 | 7952 | 4112 | 3226 | 1891 | 2887 | 2432.4056 | 327 | 488 | 1291 | 1555 | 4000.4937
2037 | 3071.2268 | 6037.3883 | 6914.5515 | 6179.4593 | 2191.5113 | 2879 | 7781 | 2342 | 2211 | 1627 | 8062 | 4179 | 3279 | 1925 | 2879 | 2426.003 | 323 | 483 | 1280 | 1541 | 4072.5026
2038 | 3107.4673 | 6093.153 | 7031.0657 | 6281.2717 | 2185.7429 | 2872 | 7921 | 2379 | 2246 | 1653 | 8166 | 4246 | 3331 | 1959 | 2872 | 2419.6173 | 320 | 479 | 1270 | 1529 | 4145.8076
2039 | 3134.2713 | 6148.969 | 7149.6533 | 6384.8633 | 2179.9896 | 2864 | 8064 | 2419 | 2284 | 1681 | 8267 | 4317 | 3387 | 1995 | 2864 | 2413.2485 | 317 | 475 | 1261 | 1519 | 4220.4322
2040 | 3171.2557 | 6204.8203 | 7270.3526 | 6490.2669 | 2174.2514 | 2856 | 8209 | 2455 | 2318 | 1706 | 8361 | 4382 | 3439 | 2031 | 2856 | 2406.8963 | 315 | 471 | 1253 | 1509 | 4296.4
2041 | 3198.8124 | 6266.2716 | 7393.2028 | 6597.5154 | 2168.5284 | 2849 | 8356 | 2499 | 2360 | 1737 | 8512 | 4461 | 3501 | 2067 | 2849 | 2400.5609 | 313 | 468 | 1246 | 1501 | 4373.7352
2042 | 3236.5583 | 6327.9248 | 7518.2439 | 6706.6427 | 2162.8204 | 2841 | 8507 | 2544 | 2403 | 1768 | 8665 | 4542 | 3564 | 2104 | 2841 | 2394.2422 | 311 | 465 | 1240 | 1493 | 4452.4624
2043 | 3264.8856 | 6389.7673 | 7645.5164 | 6817.6832 | 2157.1275 | 2834 | 8660 | 2590 | 2446 | 1800 | 8821 | 4623 | 3628 | 2142 | 2834 | 2387.9401 | 309 | 463 | 1234 | 1486 | 4532.6067
2044 | 3303.4112 | 6451.7858 | 7775.062 | 6930.6721 | 2151.4495 | 2827 | 8816 | 2637 | 2490 | 1832 | 8979 | 4707 | 3693 | 2181 | 2827 | 2381.6546 | 307 | 461 | 1229 | 1480 | 4614.1936
2045 | 3332.5274 | 6513.9667 | 7906.9227 | 7045.645 | 2145.7865 | 2819 | 8975 | 2684 | 2535 | 1865 | 9141 | 4791 | 3760 | 2220 | 2819 | 2375.3857 | 306 | 459 | 1224 | 1475 | 4697.2491
Black cells below are from "PSIP 2016 New Generation Assumptions REVISED 16-June-16.xlsx"
Size (MW) | 30 | 400 | 200 | 400 | 20 | DG-PV | 100 | 383 (3 x 1) | 152 (1 x 1) | 100 | 20 | 27 (3 x 9 MW) | 54 (6 x 9 MW) | 100 (6 x 16.8 MW) Power Barge
assumed | 30 | 400 | 200 | 400 | 20 | 0.005 | 100 | 383 | 150.586 | 100 | 20 | 27.4916 | 48.84 | 100.7184 | 0.005 | 20 | 100 | 100 | 100 | 30
Oahu 2016 Interconnect $ x 1000 | 13700 | Add $205 million (2016 $) for on-shore upgrades | NEEDS UPDATING | NEEDS UPDATING | $2,900 (46 kv) $13,700 (138 kv) | NA | Included in CapEx | 20811 | 23300 | 16200 | Included in CapEx | 13700 | 15100 | 16200
assumed | 13700 | 205000 | NA | NA | 8300 | 0 | 0 | 20811 | 23300 | 16200 | 0 | 13700 | 15100 | 16200 | 0 | 8300 | 15300 | 15300 | 15300 | 13100
| OnshoreWind | OffshoreWind | MauiOahuWind200 | MauiOahuWind400 | CentralFixedPV | FlatDistPV | SolarCSPStorage | CC_383 | CC_152 | CT_100 | Biomass | IC_MCBH | IC_Schofield | IC_Barge | SlopedDistPV | CentralTrackingPV | Battery_Conting | Battery_Reg | Battery_4 | Battery_6 | Lake_Wilson
interconnect cost per kW | 456.6667 | 512.5 | #VALUE! | #VALUE! | 415 | 0 | 0 | 54.3368 | 154.7289 | 162 | 0 | 498.3344 | 309.1728 | 160.8446 | 0 | 415 | 153 | 153 | 153 | 436.6667 | 435.8333
2016 Fixed O&M $/KW-Yr | 27.4 | 96.71 | 27.4 | 27.4 | 22.97 | NA | 92.38 | 40.3786 | 17.29 | 9.01 | 126.1 | 34.46 | 34.46 | 34.46 | NA
2016 Variable O&M $/MWH | 0 | 0 | 0 | 0 | 0 | NA | 0 | 1.085 | 4.49 | 12.99 | 66.56 | 20.96 | 20.96 | 20.96 | NA
Fixed O&M | 27.4 | 96.71 | 27.4 | 27.4 | 22.97 | 0 | 92.38 | 40.3786 | 17.29 | 9.01 | 126.1 | 34.46 | 34.46 | 34.46 | 0 | 27.4 | 5.42 | 7.61 | 19.47 | 27.49 | 42
Variable O&M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.085 | 4.49 | 12.99 | 66.56 | 20.96 | 20.96 | 20.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on O7: Barge is used primarily for HECO, but could also serve as backup for JBPHH
Note on Q8: From 2018-01-04 to 2018-07-26, this was accidentally pegged to column B instead of F, which inflated the cost by 10% in 2016 up to about 50% by 2045. This caused models run during this time to strongly prefer distributed PV over utility-scale PV, but probably didn't change overall model results by much, since distributed PV has similar cost and performance to tracking PV.
Note on Q9: See "tracking vs non-tracking PV costs.xlsx" and p. 40 of LBNL "Tracking the Sun VIII" at https://emp.lbl.gov/sites/all/files/lbnl-188238_2.pdf (Prices in 2014$.) Average ratio between cost of tracking and non-tracking systems in 2010-14 was 1.107. On the other hand, a dealer for ideematec quoted a total cost for their tracking structure and controls of $150-$250/kW, which is less than even a 10% markup. Before 2016-10-18, we used this approach (which doesn't account for future cost reductions with trackers): Average difference between tracking and non-tracking systems in 2010-14 was $0.362/Wdc (2014$). This is scaled down by 1.5 based on the DC/AC ratio used in the 2016-04-01 PSIP. This is scaled up by 1.405 to reflect the difference between Hawaii-specific costs and mainland costs, shown on p. F-4 of the 2016-04-01 PSIP. These adjustments give a total extra cost of $339 (2014$)/kW for tracking capability.
Note on V53: Assumed similar to onshore wind or large solar
Note on I55: mean value of fixed O&M and capital refurbishment from OM page of "PSIP 2016 New Generation Assumptions REVISED 16-June-16.xlsx" for 2021-45 (avg of LNG and diesel modes)
Note on I56: mean value from OM page of "PSIP 2016 New Generation Assumptions REVISED 16-June-16.xlsx" for 2021-45 (avg of LNG and diesel modes)
Note on V57: Per John Wehrheim, Pacific Hydro, personal communication, summer 2015

## PSIP storage
from "PSIP New Resource Assumptions UPDATED 11-MAR-16.xlsx" (not included in 16-June-16 workbook, not updated later) | Technology ID | Flywheel |  |  |  |  | Battery_Conting |  |  |  |  | Battery_Reg |  |  |  |  | Battery_4 |  | Res_Battery_4 | Battery_6
HAWAIIAN ELECTRIC COMPANY
2016 Power Supply Improvement Plan
Energy Storage Cost Assumptions
UPDATED MARCH 11, 2016
| Application | Inertia | Contingency |  |  |  |  | Regulation / Renewable Smoothing |  |  |  |  | Load Shifting |  |  |  |  | Residential |  | Load Shifting Long Duration |  |  | Commercial |  | Grid Support
| Size MW | 10 | 1 | 5 | 20 | 50 | 100 | 1 | 5 | 20 | 50 | 100 | 1 | 5 | 20 | 50 | 100 | 0.002 |  | 30 | 30 | 50 | 0.05 | 0.1 | 5
| Technology | Flywheel | Lithium Ion | [14 empty] | LI / NO INVERTER | LI w/ Inverter and BoP | LI | PSH | PSH | LI | LI | LI
| Duration Hours | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 4 | 4 | 4 | 4 |  | 6 | 6 | 6 | 2 | 2 | 2
| Turnaround Efficiency | 85% | 81% |  |  |  |  | 81% |  |  |  |  | 88% |  |  |  |  | 88% |  |  | 80% | 80% | 88% | 88% | 81%
| Discharge Cycles Per Year | 15000 | Up to 10 |  |  |  |  | Up to 15,000 |  |  |  |  | Up to 365 |  |  |  |  | Up to 365 |  | Up to 365 |  |  | Up to 365 |  | Up to 365
| Depth of Discharge | 100% | Up to 100% |  |  |  |  | Up to 20% |  |  |  |  | Up to 100% |  |  |  |  | Up to 100% |  | Up to 100% |  |  | Up to 100% |  | Up to 100%
| Plant Life Years | 15% | 15 |  |  |  |  | 15 |  |  |  |  | 15 |  |  |  |  | 10% |  | 15 | 40 | 40 | 10 | 10 | 15
Capital Cost in $/KILOWATT-HOUR (w/o Interconnection, w/o AFUDC)
| Install Year | [16 empty] | Storage Only | Total System
| 2016 | 9400 | 1506 | 1506 | 1506 | 1506 | 1506 | 1083 | 1083 | 1083 | 1083 | 1083 | 660 | 660 | 660 | 660 | 660 | 506 | 1026 | 530 | 583 | 583 | 553 | 553 | 1083
| 2017 | 8632 | 1383 | 1383 | 1383 | 1383 | 1383 | 999 | 999 | 999 | 999 | 999 | 615 | 615 | 615 | 615 | 615 | 465 | 961 | 493 | 594 | 594 | 511 | 511 | 999
| 2018 | 7877 | 1262 | 1262 | 1262 | 1262 | 1262 | 914 | 914 | 914 | 914 | 914 | 565 | 565 | 565 | 565 | 565 | 416 | 884 | 454 | 605 | 605 | 461 | 461 | 914
| 2019 | 7253 | 1162 | 1162 | 1162 | 1162 | 1162 | 843 | 843 | 843 | 843 | 843 | 524 | 524 | 524 | 524 | 524 | 373 | 817 | 421 | 615 | 615 | 417 | 417 | 843
| 2020 | 6729 | 1078 | 1078 | 1078 | 1078 | 1078 | 782 | 782 | 782 | 782 | 782 | 487 | 487 | 487 | 487 | 487 | 335 | 757 | 391 | 626 | 626 | 378 | 378 | 782
| 2021 | 6317 | 1012 | 1012 | 1012 | 1012 | 1012 | 737 | 737 | 737 | 737 | 737 | 461 | 461 | 461 | 461 | 461 | 317 | 729 | 371 | 638 | 638 | 359 | 359 | 737
| 2022 | 5972 | 957 | 957 | 957 | 957 | 957 | 698 | 698 | 698 | 698 | 698 | 440 | 440 | 440 | 440 | 440 | 303 | 706 | 353 | 649 | 649 | 342 | 342 | 698
| 2023 | 5678 | 910 | 910 | 910 | 910 | 910 | 666 | 666 | 666 | 666 | 666 | 422 | 422 | 422 | 422 | 422 | 290 | 687 | 339 | 661 | 661 | 328 | 328 | 666
| 2024 | 5429 | 870 | 870 | 870 | 870 | 870 | 638 | 638 | 638 | 638 | 638 | 406 | 406 | 406 | 406 | 406 | 280 | 670 | 326 | 673 | 673 | 316 | 316 | 638
| 2025 | 5214 | 835 | 835 | 835 | 835 | 835 | 614 | 614 | 614 | 614 | 614 | 393 | 393 | 393 | 393 | 393 | 270 | 655 | 316 | 685 | 685 | 305 | 305 | 614
| 2026 | 5029 | 806 | 806 | 806 | 806 | 806 | 594 | 594 | 594 | 594 | 594 | 382 | 382 | 382 | 382 | 382 | 262 | 643 | 306 | 697 | 697 | 296 | 296 | 594
| 2027 | 4869 | 780 | 780 | 780 | 780 | 780 | 576 | 576 | 576 | 576 | 576 | 372 | 372 | 372 | 372 | 372 | 256 | 632 | 298 | 710 | 710 | 289 | 289 | 576
| 2028 | 4730 | 758 | 758 | 758 | 758 | 758 | 560 | 560 | 560 | 560 | 560 | 363 | 363 | 363 | 363 | 363 | 250 | 623 | 291 | 723 | 723 | 282 | 282 | 560
| 2029 | 4609 | 738 | 738 | 738 | 738 | 738 | 547 | 547 | 547 | 547 | 547 | 355 | 355 | 355 | 355 | 355 | 245 | 615 | 285 | 736 | 736 | 276 | 276 | 547
| 2030 | 4503 | 721 | 721 | 721 | 721 | 721 | 535 | 535 | 535 | 535 | 535 | 349 | 349 | 349 | 349 | 349 | 240 | 608 | 280 | 749 | 749 | 271 | 271 | 535
| 2031 | 4409 | 706 | 706 | 706 | 706 | 706 | 525 | 525 | 525 | 525 | 525 | 343 | 343 | 343 | 343 | 343 | 236 | 601 | 275 | 762 | 762 | 267 | 267 | 525
| 2032 | 4327 | 693 | 693 | 693 | 693 | 693 | 516 | 516 | 516 | 516 | 516 | 338 | 338 | 338 | 338 | 338 | 232 | 596 | 271 | 776 | 776 | 263 | 263 | 516
| 2033 | 4255 | 682 | 682 | 682 | 682 | 682 | 508 | 508 | 508 | 508 | 508 | 333 | 333 | 333 | 333 | 333 | 229 | 591 | 268 | 790 | 790 | 259 | 259 | 508
| 2034 | 4190 | 671 | 671 | 671 | 671 | 671 | 500 | 500 | 500 | 500 | 500 | 329 | 329 | 329 | 329 | 329 | 227 | 587 | 264 | 804 | 804 | 256 | 256 | 500
| 2035 | 4133 | 662 | 662 | 662 | 662 | 662 | 494 | 494 | 494 | 494 | 494 | 326 | 326 | 326 | 326 | 326 | 224 | 583 | 262 | 819 | 819 | 253 | 253 | 494
| 2036 | 4083 | 654 | 654 | 654 | 654 | 654 | 488 | 488 | 488 | 488 | 488 | 323 | 323 | 323 | 323 | 323 | 222 | 579 | 259 | 833 | 833 | 251 | 251 | 488
| 2037 | 4038 | 647 | 647 | 647 | 647 | 647 | 483 | 483 | 483 | 483 | 483 | 320 | 320 | 320 | 320 | 320 | 220 | 576 | 257 | 848 | 848 | 249 | 249 | 483
| 2038 | 3998 | 641 | 641 | 641 | 641 | 641 | 479 | 479 | 479 | 479 | 479 | 317 | 317 | 317 | 317 | 317 | 218 | 574 | 255 | 864 | 864 | 247 | 247 | 479
| 2039 | 3962 | 635 | 635 | 635 | 635 | 635 | 475 | 475 | 475 | 475 | 475 | 315 | 315 | 315 | 315 | 315 | 217 | 571 | 253 | 879 | 879 | 245 | 245 | 475
| 2040 | 3930 | 630 | 630 | 630 | 630 | 630 | 471 | 471 | 471 | 471 | 471 | 313 | 313 | 313 | 313 | 313 | 216 | 569 | 252 | 895 | 895 | 243 | 243 | 471
| 2041 | 3902 | 625 | 625 | 625 | 625 | 625 | 468 | 468 | 468 | 468 | 468 | 312 | 312 | 312 | 312 | 312 | 214 | 567 | 250 | 911 | 911 | 242 | 242 | 468
| 2042 | 3876 | 621 | 621 | 621 | 621 | 621 | 465 | 465 | 465 | 465 | 465 | 310 | 310 | 310 | 310 | 310 | 213 | 565 | 249 | 928 | 928 | 241 | 241 | 465
| 2043 | 3854 | 617 | 617 | 617 | 617 | 617 | 463 | 463 | 463 | 463 | 463 | 309 | 309 | 309 | 309 | 309 | 212 | 564 | 248 | 944 | 944 | 240 | 240 | 463
| 2044 | 3833 | 614 | 614 | 614 | 614 | 614 | 461 | 461 | 461 | 461 | 461 | 307 | 307 | 307 | 307 | 307 | 211 | 563 | 247 | 961 | 961 | 239 | 239 | 461
| 2045 | 3815 | 611 | 611 | 611 | 611 | 611 | 459 | 459 | 459 | 459 | 459 | 306 | 306 | 306 | 306 | 306 | 211 | 561 | 246 | 979 | 979 | 238 | 238 | 459
Capital Cost in $/KILOWATT (w/o Interconnection, w/o AFUDC)
Install Year
| 2016 | 2350 | 753 | 753 | 753 | 753 | 753 | 1083 | 1083 | 1083 | 1083 | 1083 | 2640 | 2640 | 2640 | 2640 | 2640 | 2023 | 4103 | 3180 | 3500 | 3500 | 1106 | 1106 | 2166
| 2017 | 2158 | 692 | 692 | 692 | 692 | 692 | 999 | 999 | 999 | 999 | 999 | 2458 | 2458 | 2458 | 2458 | 2458 | 1858 | 3844 | 2960 | 3563 | 3563 | 1021 | 1021 | 1998
| 2018 | 1969 | 631 | 631 | 631 | 631 | 631 | 914 | 914 | 914 | 914 | 914 | 2261 | 2261 | 2261 | 2261 | 2261 | 1663 | 3536 | 2723 | 3627 | 3627 | 922 | 922 | 1827
| 2019 | 1813 | 581 | 581 | 581 | 581 | 581 | 843 | 843 | 843 | 843 | 843 | 2095 | 2095 | 2095 | 2095 | 2095 | 1492 | 3267 | 2523 | 3692 | 3692 | 834 | 834 | 1686
| 2020 | 1682 | 539 | 539 | 539 | 539 | 539 | 782 | 782 | 782 | 782 | 782 | 1948 | 1948 | 1948 | 1948 | 1948 | 1340 | 3028 | 2346 | 3759 | 3759 | 757 | 757 | 1565
| 2021 | 1579 | 506 | 506 | 506 | 506 | 506 | 737 | 737 | 737 | 737 | 737 | 1846 | 1846 | 1846 | 1846 | 1846 | 1270 | 2918 | 2223 | 3827 | 3827 | 717 | 717 | 1474
| 2022 | 1493 | 478 | 478 | 478 | 478 | 478 | 698 | 698 | 698 | 698 | 698 | 1760 | 1760 | 1760 | 1760 | 1760 | 1211 | 2825 | 2120 | 3895 | 3895 | 684 | 684 | 1397
| 2023 | 1420 | 455 | 455 | 455 | 455 | 455 | 666 | 666 | 666 | 666 | 666 | 1687 | 1687 | 1687 | 1687 | 1687 | 1161 | 2746 | 2032 | 3966 | 3966 | 656 | 656 | 1332
| 2024 | 1357 | 435 | 435 | 435 | 435 | 435 | 638 | 638 | 638 | 638 | 638 | 1625 | 1625 | 1625 | 1625 | 1625 | 1118 | 2679 | 1957 | 4037 | 4037 | 631 | 631 | 1276
| 2025 | 1304 | 418 | 418 | 418 | 418 | 418 | 614 | 614 | 614 | 614 | 614 | 1572 | 1572 | 1572 | 1572 | 1572 | 1081 | 2621 | 1893 | 4110 | 4110 | 611 | 611 | 1228
| 2026 | 1257 | 403 | 403 | 403 | 403 | 403 | 594 | 594 | 594 | 594 | 594 | 1526 | 1526 | 1526 | 1526 | 1526 | 1050 | 2572 | 1838 | 4184 | 4184 | 593 | 593 | 1187
| 2027 | 1217 | 390 | 390 | 390 | 390 | 390 | 576 | 576 | 576 | 576 | 576 | 1486 | 1486 | 1486 | 1486 | 1486 | 1023 | 2529 | 1790 | 4259 | 4259 | 577 | 577 | 1152
| 2028 | 1183 | 379 | 379 | 379 | 379 | 379 | 560 | 560 | 560 | 560 | 560 | 1452 | 1452 | 1452 | 1452 | 1452 | 999 | 2491 | 1748 | 4336 | 4336 | 564 | 564 | 1121
| 2029 | 1152 | 369 | 369 | 369 | 369 | 369 | 547 | 547 | 547 | 547 | 547 | 1422 | 1422 | 1422 | 1422 | 1422 | 978 | 2459 | 1712 | 4414 | 4414 | 552 | 552 | 1094
| 2030 | 1126 | 361 | 361 | 361 | 361 | 361 | 535 | 535 | 535 | 535 | 535 | 1395 | 1395 | 1395 | 1395 | 1395 | 960 | 2430 | 1680 | 4493 | 4493 | 542 | 542 | 1070
| 2031 | 1102 | 353 | 353 | 353 | 353 | 353 | 525 | 525 | 525 | 525 | 525 | 1372 | 1372 | 1372 | 1372 | 1372 | 944 | 2405 | 1652 | 4574 | 4574 | 533 | 533 | 1049
| 2032 | 1082 | 347 | 347 | 347 | 347 | 347 | 516 | 516 | 516 | 516 | 516 | 1352 | 1352 | 1352 | 1352 | 1352 | 930 | 2383 | 1628 | 4656 | 4656 | 525 | 525 | 1031
| 2033 | 1064 | 341 | 341 | 341 | 341 | 341 | 508 | 508 | 508 | 508 | 508 | 1334 | 1334 | 1334 | 1334 | 1334 | 917 | 2363 | 1606 | 4740 | 4740 | 518 | 518 | 1015
| 2034 | 1048 | 336 | 336 | 336 | 336 | 336 | 500 | 500 | 500 | 500 | 500 | 1318 | 1318 | 1318 | 1318 | 1318 | 907 | 2346 | 1587 | 4825 | 4825 | 512 | 512 | 1001
| 2035 | 1033 | 331 | 331 | 331 | 331 | 331 | 494 | 494 | 494 | 494 | 494 | 1304 | 1304 | 1304 | 1304 | 1304 | 897 | 2331 | 1570 | 4912 | 4912 | 506 | 506 | 988
| 2036 | 1021 | 327 | 327 | 327 | 327 | 327 | 488 | 488 | 488 | 488 | 488 | 1291 | 1291 | 1291 | 1291 | 1291 | 888 | 2317 | 1555 | 5001 | 5001 | 502 | 502 | 977
| 2037 | 1009 | 323 | 323 | 323 | 323 | 323 | 483 | 483 | 483 | 483 | 483 | 1280 | 1280 | 1280 | 1280 | 1280 | 881 | 2305 | 1541 | 5091 | 5091 | 497 | 497 | 967
| 2038 | 999 | 320 | 320 | 320 | 320 | 320 | 479 | 479 | 479 | 479 | 479 | 1270 | 1270 | 1270 | 1270 | 1270 | 874 | 2295 | 1529 | 5182 | 5182 | 493 | 493 | 958
| 2039 | 991 | 317 | 317 | 317 | 317 | 317 | 475 | 475 | 475 | 475 | 475 | 1261 | 1261 | 1261 | 1261 | 1261 | 868 | 2285 | 1519 | 5276 | 5276 | 490 | 490 | 950
| 2040 | 983 | 315 | 315 | 315 | 315 | 315 | 471 | 471 | 471 | 471 | 471 | 1253 | 1253 | 1253 | 1253 | 1253 | 862 | 2276 | 1509 | 5370 | 5370 | 487 | 487 | 943
| 2041 | 975 | 313 | 313 | 313 | 313 | 313 | 468 | 468 | 468 | 468 | 468 | 1246 | 1246 | 1246 | 1246 | 1246 | 857 | 2269 | 1501 | 5467 | 5467 | 484 | 484 | 937
| 2042 | 969 | 311 | 311 | 311 | 311 | 311 | 465 | 465 | 465 | 465 | 465 | 1240 | 1240 | 1240 | 1240 | 1240 | 853 | 2262 | 1493 | 5566 | 5566 | 482 | 482 | 931
| 2043 | 963 | 309 | 309 | 309 | 309 | 309 | 463 | 463 | 463 | 463 | 463 | 1234 | 1234 | 1234 | 1234 | 1234 | 849 | 2256 | 1486 | 5666 | 5666 | 479 | 479 | 926
| 2044 | 958 | 307 | 307 | 307 | 307 | 307 | 461 | 461 | 461 | 461 | 461 | 1229 | 1229 | 1229 | 1229 | 1229 | 846 | 2250 | 1480 | 5768 | 5768 | 478 | 478 | 921
| 2045 | 954 | 306 | 306 | 306 | 306 | 306 | 459 | 459 | 459 | 459 | 459 | 1224 | 1224 | 1224 | 1224 | 1224 | 842 | 2245 | 1475 | 5872 | 5872 | 476 | 476 | 917
Enegy Storage Construction S-Curve
Construction Year
| -6 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 5% | 5% | NA | NA | 0%
| -5 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 10% | 10% | NA | NA | 0%
| -4 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 10% | 10% | NA | NA | 0%
| -3 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NA | NA | 0% | 20% | 20% | NA | NA | 0%
| -2 | 20% | 0% | 0% | 20% | 20% | 20% | 0% | 0% | 20% | 20% | 20% | 0% | 0% | 20% | 20% | 30% | NA | NA | 30% | 30% | 30% | NA | NA | 0%
| -1 | 80% | 100% | 100% | 80% | 80% | 80% | 100% | 100% | 80% | 80% | 80% | 100% | 100% | 80% | 80% | 70% | NA | NA | 70% | 25% | 25% | NA | NA | 100%
COD
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 0% | 0% | 100%
| AFUDC Adder based on S-Curve | 4.024% | 2.461% | 2.461% | 4.024% | 4.024% | 4.024% | 2.461% | 2.461% | 4.024% | 4.024% | 4.024% | 2.461% | 2.461% | 4.024% | 4.024% | 4.806% | NA | NA | 4.81% | 16.36% | 16.36% | NA | NA | 2.46%
Enegy Storage Interconnection and O&M Costs
| Oahu Interconnection Cost 2016 $x1000 | 2700 | NA | 2700 | $2,700 46 KV / $13,100 138 KV | 14200 | 15300 | NA | 2700 | $2,700 46 KV / $13,100 138 KV | 14200 | 15300 | NA | 2700 | $2,700 46 KV $13,100 138 KV | 14200 | 15300 | NA | NA | 13100 | 13100 | 14200 | NA | NA | 2700
| Escalator | 1.8% | NA | 1.8% | 1.8% | 1.8% | 1.8% | NA | 1.8% | 1.8% | 1.8% | 1.8% | NA | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8%
| Maui Interconnection Costs $2016 $x1000 | 7500 | 2000 | 7500 | 6000 | NA | NA | 2000 | 7500 | 6000 | NA | NA | 2000 | 7500 | 5500 | NA | NA | NA | NA | 6000 | 6000 | NA | NA | NA | 7500
| Escalator | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | NA | NA | 1.8% | 1.8% | NA | NA | NA | 1.8%
| Hawaii Interconnection Costs 2016 $x1000 | 3000 | 200 | 2120 | 5500 | NA | NA | 200 | 2120 | 5500 | NA | NA | 200 | 2120 | 5500 | NA | NA | NA | NA | 5500 | 5500 | NA | NA | NA | 2120
| Escalator | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | NA | NA | 1.8% | 1.8% | NA | NA | NA | 1.8%
| Fixed O&M 2016 $/KW-Yr |  | 89.08 | 21.26 | 8.95 | 6.37 | 5.42 | 91.41 | 23.58 | 11.27 | 8.7 | 7.61 | 103.12 | 35.3 | 22.99 | 20.41 | 19.47 | NA | NA | 27.49 | 30 | 30 | NA | NA | 28.81
| Escalator | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | 1.8% | NA | NA | 1.8% | 1.8% | 1.8% | NA | NA | 1.8%
Changes and modifications
|  | 2016-02-29 | HDB | Updated interconnection costs for Oahu to reflect removal of land costs from substation cost estimate (assumes BESS project includes land.
|  | 2016-03-11 | HDB | Updated BESS + inverter cost for residential energy storage to reflect changes received from BCG.
|  | 2016-03-11 | HDB | Added row for AFUDC factors being used by planning teams
| assumed size | 10 | 1 | 5 | 20 | 50 | 100 | 1 | 5 | 20 | 50 | 100 | 1 | 5 | 20 | 50 | 100 | 0.002 | 0 | 30 | 30 | 50 | 0.05 | 0.1 | 5
| assumed cost | 2700 | NA | 2700 | $2,700 46 KV / $13,100 138 KV | 14200 | 15300 | NA | 2700 | $2,700 46 KV / $13,100 138 KV | 14200 | 15300 | NA | 2700 | $2,700 46 KV $13,100 138 KV | 14200 | 15300 | NA | NA | 13100 | 13100 | 14200 | NA | NA | 2700
|  | Flywheel | 0 | 0 | 0 | 0 | Battery_Conting | 0 | 0 | 0 | 0 | Battery_Reg | 0 | 0 | 0 | 0 | Battery_4 | 0 | Res_Battery_4 | Battery_6 | 0 | 0 | 0 | 0 | 0
| interconnect cost per kW | 270 | #VALUE! | 540 | #VALUE! | 284 | 153 | #VALUE! | 540 | #VALUE! | 284 | 153 | #VALUE! | 540 | #VALUE! | 284 | 153 | #VALUE! | #VALUE! | 436.6667 | 436.6667 | 284 | #VALUE! | #VALUE! | 540
| Fixed O&M ($/kW-y) | 0 | 89.08 | 21.26 | 8.95 | 6.37 | 5.42 | 91.41 | 23.58 | 11.27 | 8.7 | 7.61 | 103.12 | 35.3 | 22.99 | 20.41 | 19.47 | NA | NA | 27.49 | 30 | 30 | NA | NA | 28.81
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| lifetime (years) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| hours of service | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 6 | 6 | 6 | 2 | 2 | 2
Note on C130: We model the pure-reserve batteries as having zero hours of storage, so they can provide reserve power but no energy shifting.

## sales
load_zone | year | underlying forecast (GWh) | energy efficiency (GWh) | underlying forecast (MW) | energy efficiency (MW)
Oahu | 2016 | 8286 | -1076.9 | 1363.7 | -198.7 | 0.1616
Oahu | 2017 | 8481.3 | -1149 | 1397.7 | -215.7 | 0.1612
Oahu | 2018 | 8691.4 | -1223.6 | 1431.7 | -232.7 | 0.16056
Oahu | 2019 | 8816.8 | -1287.8 | 1447.7 | -248.7 | 0.15925
Oahu | 2020 | 8885.6 | -1375.1 | 1454.7 | -266.7 | 0.15818
Oahu | 2021 | 8933.4 | -1465.8 | 1465.7 | -284.7 | 0.15815
Oahu | 2022 | 8952.7 | -1556.6 | 1468.7 | -302.7 | 0.15765
Oahu | 2023 | 8987 | -1647.4 | 1473.7 | -321.7 | 0.15696
Oahu | 2024 | 9053.7 | -1744.1 | 1479.7 | -344.7 | 0.15528
Oahu | 2025 | 9087.4 | -1846 | 1488.7 | -369.7 | 0.15453
Oahu | 2026 | 9154 | -1957 | 1499.7 | -400.7 | 0.1527
Oahu | 2027 | 9229.7 | -2079.5 | 1511.7 | -436.7 | 0.15035
Oahu | 2028 | 9329.1 | -2209.1 | 1524.7 | -474.7 | 0.14747
Oahu | 2029 | 9376.6 | -2345.6 | 1534.7 | -516.7 | 0.14479
Oahu | 2030 | 9459.9 | -2486 | 1547.7 | -560.7 | 0.14153
Oahu | 2031 | 9513.1 | -2552.8 | 1555.7 | -568.7 | 0.1418
Oahu | 2032 | 9581.3 | -2561.4 | 1563.7 | -570.7 | 0.14146
Oahu | 2033 | 9604.9 | -2567.8 | 1570.7 | -571.7 | 0.14196
Oahu | 2034 | 9651.7 | -2573.6 | 1578.7 | -573.7 | 0.14199
Oahu | 2035 | 9703.5 | -2584.1 | 1586.7 | -576.7 | 0.14187
Oahu | 2036 | 9785.3 | -2600.8 | 1595.7 | -581.7 | 0.14114
Oahu | 2037 | 9823.4 | -2615.4 | 1605.7 | -583.7 | 0.14179
Oahu | 2038 | 9885.8 | -2628.1 | 1615.7 | -587.7 | 0.14164
Oahu | 2039 | 9947.4 | -2644.4 | 1625.7 | -591.7 | 0.14159
Oahu | 2040 | 10031.6 | -2664.9 | 1634.7 | -596.7 | 0.1409
Oahu | 2041 | 10065.8 | -2680.1 | 1643.7 | -599.7 | 0.14135
Oahu | 2042 | 10122.3 | -2691.8 | 1651.7 | -602.7 | 0.14117
Oahu | 2043 | 10178 | -2707.1 | 1660.7 | -606.7 | 0.14108
Oahu | 2044 | 10256.7 | -2726.4 | 1670.7 | -611.7 | 0.14063
Oahu | 2045 | 10287.7 | -2741.4 | 1679.7 | -614.7 | 0.14113
Note on C1: from 2016-04-01 PSIP Book 1, p. J-44 and 2016-12-23 PSIP Book 3, p. J-45
Note on D1: from 2016-04-01 PSIP Book 1, p. J-44 and 2016-12-23 PSIP Book 3, p. J-45
Note on E1: from 2016-04-01 PSIP Book 1, p. J-49 and 2016-12-23 PSIP Book 3, p. J-50
Note on F1: from 2016-04-01 PSIP Book 1, p. J-49 and 2016-12-23 PSIP Book 3, p. J-50

## DistPV
year | dist PV total | year | addition | tuple
2016 | 443.9935 | 2016 | 443.9935 | (2016, 'DistPV', 443.993468266547),
2017.0012 | 536.7452 | 2017 | 92.7518 | (2017, 'DistPV', 92.751756737742),
2018.0342 | 564.0235 | 2018 | 27.2782 | (2018, 'DistPV', 27.278236032368),
2019.0195 | 590.2116 | 2019 | 26.1881 | (2019, 'DistPV', 26.188129564885),
2019.9889 | 612.0361 | 2020 | 21.8245 | (2020, 'DistPV', 21.8245069017911),
2021.0061 | 627.3104 | 2021 | 15.2743 | (2021, 'DistPV', 15.27427771741),
2022.0232 | 639.3143 | 2022 | 12.004 | (2022, 'DistPV', 12.0039583149589),
2023.0085 | 650.225 | 2023 | 10.9107 | (2023, 'DistPV', 10.910655054315),
2024.0097 | 661.1388 | 2024 | 10.9139 | (2024, 'DistPV', 10.913851847475),
2024.995 | 672.0495 | 2025 | 10.9107 | (2025, 'DistPV', 10.910655054316),
2025.9962 | 681.87 | 2026 | 9.8205 | (2026, 'DistPV', 9.82054858683205),
2027.0133 | 692.7807 | 2027 | 10.9107 | (2027, 'DistPV', 10.910655054316),
2028.0145 | 703.6914 | 2028 | 10.9107 | (2028, 'DistPV', 10.910655054315),
2028.9999 | 717.8787 | 2029 | 14.1874 | (2029, 'DistPV', 14.1873680430859),
2030.017 | 727.6993 | 2030 | 9.8205 | (2030, 'DistPV', 9.82054858683205),
2031.0183 | 738.6131 | 2031 | 10.9139 | (2031, 'DistPV', 10.913851847475),
2032.0036 | 748.4337 | 2032 | 9.8205 | (2032, 'DistPV', 9.82054858683193),
2032.9889 | 762.6178 | 2033 | 14.1842 | (2033, 'DistPV', 14.1841712499261),
2034.006 | 770.2582 | 2034 | 7.6403 | (2034, 'DistPV', 7.64033565186492),
2034.9755 | 783.3522 | 2035 | 13.0941 | (2035, 'DistPV', 13.094064782442),
2036.0084 | 793.1728 | 2036 | 9.8205 | (2036, 'DistPV', 9.82054858683205),
2037.0095 | 804.093 | 2037 | 10.9202 | (2037, 'DistPV', 10.9202454337949),
2037.9949 | 813.7629 | 2038 | 9.6699 | (2038, 'DistPV', 9.66989970917803),
2039.0369 | 825.9143 | 2039 | 12.1514 | (2039, 'DistPV', 12.1514103994531),
2039.9974 | 838.1541 | 2040 | 12.2397 | (2040, 'DistPV', 12.2397218104919),
2040.9986 | 849.9215 | 2041 | 11.7674 | (2041, 'DistPV', 11.7673956211361),
2042.0156 | 860.8321 | 2042 | 10.9107 | (2042, 'DistPV', 10.9106550543149),
2043.0328 | 870.6527 | 2043 | 9.8205 | (2043, 'DistPV', 9.82054858683205),
2044.034 | 885.9301 | 2044 | 15.2775 | (2044, 'DistPV', 15.27747451057),
2045 | 896.2218 | 2045 | 10.2917 | (2045, 'DistPV', 10.291675978754),

## heat rates
technology | load level (MW) | fuel consumption (MMBtu/h) | lookup | CC 152 data - from PSIP 2016 New Generation Assumptions REVISED 16-June-16.xlsx, sheet "CT & CC Op Parameters"
CC_152 | 71.162 | 569.8653 | " | load level (MW) | avg heat rate (Btu/kWh)
CC_152 | 87.949 | 661.2885 | " | 71.162 | 8008
CC_152 | 113.972 | 812.1645 | " | 87.949 | 7519
CC_152 | 116.985 | 832.2313 | " | 113.972 | 7126
CC_152 | 150.586 | 1072.4614 | CC_152 | 116.985 | 7114
IC_MCBH | 2.7333 | 30.885 | " | 143.858 | 7455
IC_MCBH | 9.1639 | 79.4875 | IC_MCBH | 150.586 | 7478
IC_Schofield | 2.7333 | 30.885 | "
IC_Schofield | 8.14 | 71.4075 | IC_Schofield | 9 MW Wartsila units (MCBH)
IC_Barge | 5.023 | 53.6647 | " | Generator set load (%) | 100 | 90 | 80 | 70 | 60 | 50
IC_Barge | 16.7864 | 143.1267 | IC_Barge | Genset gross output | 9370 | 8432 | 7492 | 6550 | 5605 | 4658 | kWe
|  |  |  | Genset net output | 9163.86 | 8246.496 | 7327.176 | 6405.9 | 5481.69 | 4555.524 | kWe
|  |  |  | 20V34DF Gross heat rate (LHV) | 7555 | 7659 | 7920 | 8289 | 8611 | 8969 | BTU/kWh | GAS OPERATION
|  |  |  | 20V34DF Net heat rate (HHV) | 8574.6933 | 8692.7301 | 8988.9571 | 9407.7607 | 9773.2209 | 10179.5399 | BTU/kWh | GAS OPERATION
|  |  |  | 20V34DF Gross heat rate (LHV) | 8019 | 7909 | 8017 | 8238 | 8328 | 8434 | BTU/kWh | LIQUID FUEL OPERATION
|  |  |  | 20V34DF Net heat rate (HHV) | 8773.3436 | 8652.9959 | 8771.1554 | 9012.9448 | 9111.411 | 9227.3824 | BTU/kWh | LIQUID FUEL OPERATION
reserve cost
|  |  |  | output (MW) | 9.1639 | 8.2465 | 7.3272 | 6.4059 | 5.4817 | 4.5555 | 2.7333 | MW | 7.4949 | 10.3991 | 0.13083
|  |  |  | total MMBtu (avg of gas and liquid) | 79.4875 | 71.5207 | 65.0657 | 59.0006 | 51.7598 | 44.2044 | 30.885 | MMBtu/h | 0.14412 | 1.0149
|  |  |  | linear fit | 79.0812 | 72.2056 | 65.3154 | 58.4106 | 51.4837 | 44.5422 | 30.885 | MMBtu/h | 0.99852 | 0.55567
|  |  |  | inc heat rate | 8.6844 | 7.0215 | 6.5834 | 7.8345 | 8.1578 | 7.3095
16.8 MW Wartsila units (power barge)
|  |  |  | Generator set load (%) | 100 | 90 | 80 | 70 | 60 | 50 | 40
|  |  |  | Genset gross output | 17164 | 15452 | 13736 | 12015 | 10290 | 8560 | 6826 | kWe
|  |  |  | Genset net output | 16786.392 | 15112.056 | 13433.808 | 11750.67 | 10063.62 | 8371.68 | 6675.828 | kWe
|  |  |  | 18V50DF Gross heat rate (LHV) | 7530 | 7512 | 7704 | 7953 | 8218 | 8508 | 9198 | BTU/kWh | GAS OPERATION
|  |  |  | 18V50DF Net heat rate (HHV) | 8546.319 | 8525.8896 | 8743.8037 | 9026.411 | 9327.1779 | 9656.319 | 10439.4479 | BTU/kWh | GAS OPERATION
|  |  |  | 18V50DF Gross heat rate (LHV) | 7775 | 7777 | 7850 | 7996 | 8175 | 8407 | 8735 | BTU/kWh | LIQUID FUEL OPERATION
|  |  |  | 18V50DF Net heat rate (HHV) | 8506.3906 | 8508.5787 | 8588.4458 | 8748.18 | 8944.0184 | 9197.8425 | 9556.6973 | BTU/kWh | LIQUID FUEL OPERATION
reserve cost
|  |  |  | output (MW) | 16.7864 | 15.1121 | 13.4338 | 11.7507 | 10.0636 | 8.3717 | 5.023 | MW | 7.5266 | 15.8584 | 0.1108
|  |  |  | total MMBtu (avg of gas and liquid) | 143.1267 | 128.7129 | 116.4191 | 104.4317 | 91.9372 | 78.9205 | 53.6647 | MMBtu/h | 0.10233 | 1.3211
|  |  |  | linear fit | 136.2111 | 123.6622 | 111.0839 | 98.469 | 85.8248 | 73.1439 | 53.6647 | MMBtu/h | 0.99926 | 0.7204
|  |  |  | inc heat rate | 8.6087 | 7.3254 | 7.122 | 7.4061 | 7.6933 | 7.542
Note on B7: We skip the second-to-last step, because it is non-convex and it's unclear whether it could be swapped with the last step (so we assume both duct burners and wet compression are engaged). It's actually unclear whether the table shows DB before or after WC, since the second-to-last step is labled as DB but shows the same jump in fuel as the WC step for the 3x1, for the raw CT and ST, but not the CC trains.
Note on B8: We only use lowest and highest because heat rate is very nearly linear but is slighly nonconvex in the middle.
Note on B10: Assumed same minimum load as later model.
Note on B11: This is 8.14 MW per unit according to GE RPS study and Plexos input files at data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/DBEDT-IR-12/Input/Oahu/Oahu E3 Plan Input/CSV files/PSIP Max Capacity.csv. Also note: PSIP xlsx file says for MCBH: "These numbers are for the "new" 20V34DF, not the Schofield units". (Schofield also uses 34DF, per http://www.wartsila.com/media/news/27-10-2014-wartsila-supplies-50-mw-power-plant-to-help-integration-of-solar-energy-in-hawaii). Permit application to Hawaii Department of Health also says these gens have peak output of 8.3-8.4 MW with implied heat rate of 8.6 MMBtu/MWh.
Note on C11: Assumed same heat rate as later model at MCBH; also matches permit application at http://health.hawaii.gov/cab/files/2016/03/0793-01.review.DRAFT_.ms_.pdf
Note on B12: We only use lowest and highest because heat rate is very nearly linear but is slighly nonconvex in the middle.
Note on O20: Minimum load per unit is 30% per http://www.wartsila.com/docs/default-source/Power-Plants-documents/reference-documents/power-plants-solutions-catalogue/pps2015_lowres.pdf?sfvrsn=2
Note on O34: Minimum load per unit is 30% per http://www.wartsila.com/docs/default-source/Power-Plants-documents/reference-documents/power-plants-solutions-catalogue/pps2015_lowres.pdf?sfvrsn=2

## ATB
| From NREL Annual Technology Baseline, https://atb.nrel.gov |  |  |  |  | Note: ATB 2019 costs are in 2017$ but PSIP is in 2016$
| cost base year | 2017
| Technology | CentralTrackingPV | FlatDistPV | SlopedDistPV | OnshoreWind | OffshoreWind | Battery_Bulk | Battery_Reg | Battery_Conting
| asset life (years) | 30 | 30 | 30 | 30 | 30 | 15 | 15 | 15
| Capital cost adder for Honolulu | 64% | 62% | 62% | 35% | 35% | 28% | 28% | 28%
| DC-AC ratio | 1.3 | 1.15 | 1.15 | [5 empty] | <--- implemented directly in import code, not read from here
| inverter efficiency | 98% | 98% | 98% | [5 empty] | <--- implemented directly in import code, not read from here
| panel efficiency | 19.1% | 19.1% | 17.2% | [5 empty] | <--- implemented directly in import code, not read from here
| pre-inverter efficiency | 9.5% | 9.5% | 9.5% | [5 empty] | <--- implemented directly in import code, not read from here
| annual degradation | 0.75% | 0.75% | 0.75%
| degradation de-rate | 89.85% | 89.85% | 89.85% | [5 empty] | <--- implemented directly in import code, not read from here
| total losses incl. degradation | 18.69% | 18.69% | 18.69%
| round-trip efficiency | [5 empty] | 90% | 90% | 90%
National capital cost in 2017$ (ATB base year) (including construction, excluding tax credits and new trade tariffs from 2018) (see below for regional values)
ATB Scenario | Technology | Scenario | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
RL3UtLosAngs | CentralTrackingPV | ATB_2019_low | 1110.7302 | 1114.7551 | 961.6048 | 902.2265 | 868.4703 | 834.7141 | 800.9578 | 767.2016 | 733.4454 | 699.6892 | 665.933 | 632.1768 | 598.4206 | 564.6644 | 548.5147 | 532.365 | 516.2153 | 500.0656 | 483.9159 | 471.6619 | 459.4079 | 447.1539 | 434.8999 | 422.6459 | 415.2131 | 407.7804 | 400.3477 | 392.915 | 385.4823 | 379.5794 | 373.6766 | 367.7737 | 361.8709 | 355.968
RM3UtLosAngs | CentralTrackingPV | ATB_2019_mid | 1110.7302 | 1114.7551 | 1095.1363 | 1074.5461 | 1054.2716 | 1032.8708 | 1011.47 | 990.0692 | 968.6684 | 947.2675 | 925.8667 | 904.4659 | 883.0651 | 861.6643 | 852.1114 | 842.5586 | 833.0057 | 823.4529 | 813.9 | 804.3472 | 794.7943 | 785.2415 | 775.6886 | 766.1358 | 757.8532 | 749.5707 | 741.2881 | 733.0056 | 724.723 | 716.4405 | 708.1579 | 699.8754 | 691.5928 | 683.3103
RC3UtLosAngs | CentralTrackingPV | ATB_2019_high | 1110.7302 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551 | 1114.7551
RL3CoLosAngs | FlatDistPV | ATB_2019_low | 1857.0002 | 1810.0138 | 1332.6953 | 1247.9067 | 1122.8106 | 1084.7034 | 1046.5961 | 1008.4888 | 970.3815 | 932.2742 | 894.1669 | 856.0596 | 817.9523 | 779.845 | 760.7636 | 741.6821 | 722.6007 | 703.5192 | 684.4378 | 665.3563 | 646.2749 | 627.1934 | 608.112 | 589.0305 | 583.8548 | 578.679 | 573.5033 | 568.3275 | 543.0868 | 541.924 | 540.7613 | 539.5985 | 538.4358 | 537.273
RM3CoLosAngs | FlatDistPV | ATB_2019_mid | 1857.0002 | 1810.0138 | 1722.5136 | 1622.8671 | 1599.8773 | 1562.908 | 1525.9387 | 1488.9693 | 1452 | 1415.0307 | 1378.0614 | 1341.092 | 1304.1227 | 1267.1534 | 1255.2276 | 1243.3019 | 1231.3762 | 1219.4504 | 1207.5247 | 1195.5989 | 1183.6732 | 1171.7475 | 1159.8217 | 1147.896 | 1134.4787 | 1121.0613 | 1107.644 | 1094.2267 | 1080.8093 | 1067.392 | 1053.9747 | 1040.5574 | 1027.14 | 1013.7227
RC3CoLosAngs | FlatDistPV | ATB_2019_high | 1857.0002 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138 | 1810.0138
RL3ReLosAngs | SlopedDistPV | ATB_2019_low | 2769.7352 | 2639.7973 | 2346.066 | 2217.0323 | 2075.6523 | 1934.2723 | 1792.8922 | 1651.5122 | 1510.1321 | 1368.7521 | 1227.372 | 1085.992 | 944.6119 | 803.2319 | 783.7623 | 764.2927 | 744.8231 | 725.3535 | 705.8839 | 686.4143 | 666.9447 | 647.4752 | 628.0056 | 608.536 | 599.2235 | 589.9111 | 580.5987 | 571.2862 | 561.9738 | 559.579 | 557.1843 | 554.7895 | 552.3948 | 550
RM3ReLosAngs | SlopedDistPV | ATB_2019_mid | 2769.7352 | 2639.7973 | 2575.3202 | 2510.8431 | 2400.6082 | 2290.3733 | 2180.1384 | 2069.9035 | 1959.6686 | 1849.4337 | 1739.1988 | 1628.9639 | 1518.729 | 1408.4941 | 1381.7373 | 1354.9804 | 1328.2236 | 1301.4667 | 1274.7099 | 1247.953 | 1221.1962 | 1194.4393 | 1167.6825 | 1140.9256 | 1129.4438 | 1117.9619 | 1106.48 | 1094.9982 | 1083.5163 | 1080.8131 | 1078.1098 | 1075.4065 | 1072.7033 | 1070
RC3ReLosAngs | SlopedDistPV | ATB_2019_high | 2769.7352 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973 | 2639.7973
RL3LaLTRG11 | OnshoreWind | ATB_2019_low | 1610.1086 | 1572.7557 | 1535.4027 | 1498.0498 | 1460.6968 | 1423.3439 | 1385.9909 | 1348.638 | 1311.285 | 1273.9321 | 1236.5791 | 1199.2262 | 1161.8732 | 1124.5203 | 1109.4955 | 1094.4145 | 1079.2774 | 1064.0842 | 1048.8348 | 1033.5294 | 1018.1677 | 1002.75 | 987.2761 | 971.7461 | 956.16 | 940.5177 | 924.8193 | 909.0648 | 893.2541 | 877.3873 | 861.4644 | 845.4853 | 829.4501 | 813.3588
RM3LaLTRG11 | OnshoreWind | ATB_2019_mid | 1610.1086 | 1582.5854 | 1555.0622 | 1527.5389 | 1500.0157 | 1472.4925 | 1444.9693 | 1417.446 | 1389.9228 | 1362.3996 | 1334.8764 | 1307.3531 | 1279.8299 | 1252.3067 | 1238.7803 | 1225.2333 | 1211.6657 | 1198.0774 | 1184.4686 | 1170.8391 | 1157.189 | 1143.5182 | 1129.8269 | 1116.1149 | 1102.3824 | 1088.6292 | 1074.8554 | 1061.0609 | 1047.2459 | 1033.4102 | 1019.5539 | 1005.677 | 991.7795 | 977.8613
RC3LaLTRG11 | OnshoreWind | ATB_2019_high | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086 | 1610.1086
RL3OfOTRG66 | OffshoreWind | ATB_2019_low | 5532.0294 | 4266.6605 | 4114.1272 | 3967.7579 | 3827.2977 | 3692.5023 | 3563.1376 | 3438.9792 | 3319.8119 | 3205.4297 | 3095.6348 | 2990.2378 | 2889.0573 | 2791.9192 | 2698.6566 | 2609.1098 | 2523.1254 | 2440.5566 | 2361.2625 | 2285.1083 | 2211.9646 | 2141.7073 | 2074.2177 | 2009.3817 | 1947.0904 | 1887.2388 | 1829.7269 | 1774.4583 | 1721.3409 | 1670.2864 | 1621.21 | 1574.0306 | 1528.6704 | 1485.0548
RM3OfOTRG66 | OffshoreWind | ATB_2019_mid | 5532.0294 | 5333.3256 | 5142.6591 | 4959.6974 | 4784.1222 | 4615.6279 | 4453.922 | 4298.724 | 4149.7649 | 4006.7871 | 3869.5435 | 3737.7973 | 3611.3216 | 3489.899 | 3373.3208 | 3261.3872 | 3153.9067 | 3050.6957 | 2951.5782 | 2856.3854 | 2764.9557 | 2677.1341 | 2592.7721 | 2511.7272 | 2433.8629 | 2359.0485 | 2287.1586 | 2218.0728 | 2151.6761 | 2087.8579 | 2026.5125 | 1967.5383 | 1910.838 | 1856.3185
RC3OfOTRG66 | OffshoreWind | ATB_2019_high | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294 | 5532.0294
| Battery_Bulk | ATB_2019_low | 667.9688 | 667.9688 | 595.3934 | 522.8181 | 482.8938 | 442.9695 | 403.0452 | 363.1209 | 323.1966 | 302.2839 | 281.3712 | 260.4585 | 239.5457 | 218.633 | 214.3554 | 210.0778 | 205.8002 | 201.5226 | 197.245 | 192.9674 | 188.6898 | 184.4122 | 180.1346 | 175.857 | 171.5794 | 167.3018 | 163.0242 | 158.7466 | 154.469 | 150.1914 | 145.9138 | 141.6362 | 137.3586 | 133.081
| Battery_Bulk | ATB_2019_mid | 667.9688 | 667.9688 | 622.899 | 577.8292 | 549.3437 | 520.8581 | 492.3725 | 463.887 | 435.4014 | 421.2518 | 407.1021 | 392.9525 | 378.8028 | 364.6532 | 360.095 | 355.5369 | 350.9787 | 346.4205 | 341.8624 | 337.3042 | 332.746 | 328.1879 | 323.6297 | 319.0715 | 314.5134 | 309.9552 | 305.3971 | 300.8389 | 296.2807 | 291.7226 | 287.1644 | 282.6062 | 278.0481 | 273.4899
| Battery_Bulk | ATB_2019_high | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688 | 667.9688
| Battery_Conting | ATB_2019_low | 770.0195 | 770.0195 | 686.3563 | 602.6931 | 556.6692 | 510.6454 | 464.6216 | 418.5977 | 372.5739 | 348.4662 | 324.3584 | 300.2507 | 276.143 | 252.0353 | 247.1042 | 242.173 | 237.2419 | 232.3108 | 227.3797 | 222.4485 | 217.5174 | 212.5863 | 207.6552 | 202.724 | 197.7929 | 192.8618 | 187.9307 | 182.9995 | 178.0684 | 173.1373 | 168.2062 | 163.275 | 158.3439 | 153.4128
| Battery_Conting | ATB_2019_mid | 770.0195 | 770.0195 | 718.0641 | 666.1087 | 633.2712 | 600.4336 | 567.5961 | 534.7586 | 501.9211 | 485.6097 | 469.2983 | 452.9869 | 436.6755 | 420.3641 | 415.1096 | 409.855 | 404.6004 | 399.3459 | 394.0913 | 388.8368 | 383.5822 | 378.3277 | 373.0731 | 367.8186 | 362.564 | 357.3095 | 352.0549 | 346.8004 | 341.5458 | 336.2913 | 331.0367 | 325.7822 | 320.5276 | 315.2731
| Battery_Conting | ATB_2019_high | 770.0195 | 770.0195 | 770.0195 | 764.2971 | 762.7423 | 761.1874 | 759.6326 | 758.0778 | 756.523 | 754.9682 | 753.4134 | 751.8586 | 750.3038 | 748.749 | 748.2441 | 747.7392 | 747.2344 | 746.7295 | 746.2246 | 745.7197 | 745.2149 | 744.71 | 744.2051 | 743.7002 | 743.1954 | 742.6905 | 742.1856 | 741.6807 | 741.1758 | 740.671 | 740.1661 | 739.6612 | 739.1563 | 738.6515
| Battery_Reg | ATB_2019_low | 872.0703 | 872.0703 | 777.3192 | 682.568 | 630.4447 | 578.3213 | 526.1979 | 474.0745 | 421.9511 | 394.6484 | 367.3457 | 340.043 | 312.7403 | 285.4375 | 279.8529 | 274.2682 | 268.6836 | 263.099 | 257.5143 | 251.9297 | 246.345 | 240.7604 | 235.1757 | 229.5911 | 224.0064 | 218.4218 | 212.8371 | 207.2525 | 201.6678 | 196.0832 | 190.4985 | 184.9139 | 179.3292 | 173.7446
| Battery_Reg | ATB_2019_mid | 872.0703 | 872.0703 | 813.2292 | 754.3881 | 717.1987 | 680.0092 | 642.8197 | 605.6302 | 568.4407 | 549.9676 | 531.4944 | 513.0213 | 494.5481 | 476.075 | 470.1241 | 464.1731 | 458.2222 | 452.2713 | 446.3203 | 440.3694 | 434.4184 | 428.4675 | 422.5166 | 416.5656 | 410.6147 | 404.6638 | 398.7128 | 392.7619 | 386.8109 | 380.86 | 374.9091 | 368.9581 | 363.0072 | 357.0563
| Battery_Reg | ATB_2019_high | 872.0703 | 872.0703 | 872.0703 | 860.6254 | 857.5158 | 854.4061 | 851.2965 | 848.1869 | 845.0773 | 841.9677 | 838.8581 | 835.7485 | 832.6389 | 829.5292 | 828.5195 | 827.5097 | 826.5 | 825.4902 | 824.4805 | 823.4707 | 822.461 | 821.4512 | 820.4415 | 819.4317 | 818.422 | 817.4122 | 816.4024 | 815.3927 | 814.3829 | 813.3732 | 812.3634 | 811.3537 | 810.3439 | 809.3342
Generic storage energy capital cost ($/kWh) (see below for regional values)
| Technology | Scenario | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Battery_Bulk | ATB_2019_low | 204.1016 | 204.1016 | 181.9258 | 159.75 | 147.5509 | 135.3518 | 123.1527 | 110.9536 | 98.7545 | 92.3645 | 85.9745 | 79.5845 | 73.1945 | 66.8045 | 65.4975 | 64.1904 | 62.8834 | 61.5764 | 60.2693 | 58.9623 | 57.6552 | 56.3482 | 55.0411 | 53.7341 | 52.427 | 51.12 | 49.8129 | 48.5059 | 47.1989 | 45.8918 | 44.5848 | 43.2777 | 41.9707 | 40.6636
| Battery_Bulk | ATB_2019_mid | 204.1016 | 204.1016 | 190.3302 | 176.5589 | 167.855 | 159.1511 | 150.4472 | 141.7432 | 133.0393 | 128.7158 | 124.3923 | 120.0688 | 115.7453 | 111.4218 | 110.029 | 108.6363 | 107.2435 | 105.8507 | 104.4579 | 103.0652 | 101.6724 | 100.2796 | 98.8869 | 97.4941 | 96.1013 | 94.7085 | 93.3158 | 91.923 | 90.5302 | 89.1374 | 87.7447 | 86.3519 | 84.9591 | 83.5664
| Battery_Bulk | ATB_2019_high | 204.1016 | 204.1016 | 204.1016 | 192.6566 | 189.547 | 186.4374 | 183.3278 | 180.2182 | 177.1086 | 173.9989 | 170.8893 | 167.7797 | 164.6701 | 161.5605 | 160.5507 | 159.541 | 158.5312 | 157.5215 | 156.5117 | 155.502 | 154.4922 | 153.4825 | 152.4727 | 151.463 | 150.4532 | 149.4435 | 148.4337 | 147.4239 | 146.4142 | 145.4044 | 144.3947 | 143.3849 | 142.3752 | 141.3654
| Battery_Conting | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Conting | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Conting | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M ($/kW-year) | NOTE: ATB 2019 summary sheet combines fixed and variable O&M into a single number; we use that number for fixed O&M and zero out variable O&M, since that is always zero; double-check in future years
| Technology | Scenario | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
RL3UtLosAngs | CentralTrackingPV | ATB_2019_low | 19.8672 | 13.8029 | 11.3831 | 10.6802 | 10.2806 | 9.881 | 9.4814 | 9.0818 | 8.6822 | 8.2826 | 7.883 | 7.4834 | 7.0838 | 6.6842 | 6.4931 | 6.3019 | 6.1107 | 5.9196 | 5.7284 | 5.5833 | 5.4383 | 5.2932 | 5.1482 | 5.0031 | 4.9151 | 4.8271 | 4.7391 | 4.6512 | 4.5632 | 4.4933 | 4.4234 | 4.3535 | 4.2837 | 4.2138
RM3UtLosAngs | CentralTrackingPV | ATB_2019_mid | 19.8672 | 13.8029 | 12.9637 | 12.72 | 12.48 | 12.2267 | 11.9733 | 11.72 | 11.4667 | 11.2133 | 10.96 | 10.7067 | 10.4533 | 10.2 | 10.0869 | 9.9738 | 9.8608 | 9.7477 | 9.6346 | 9.5215 | 9.4084 | 9.2953 | 9.1823 | 9.0692 | 8.9711 | 8.8731 | 8.775 | 8.677 | 8.5789 | 8.4809 | 8.3829 | 8.2848 | 8.1868 | 8.0887
RC3UtLosAngs | CentralTrackingPV | ATB_2019_high | 19.8672 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029 | 13.8029
RL3CoLosAngs | FlatDistPV | ATB_2019_low | 17.9354 | 17.1023 | 13.1465 | 12.3101 | 11.0761 | 10.7002 | 10.3243 | 9.9484 | 9.5725 | 9.1965 | 8.8206 | 8.4447 | 8.0688 | 7.6929 | 7.5047 | 7.3164 | 7.1282 | 6.94 | 6.7517 | 6.5635 | 6.3753 | 6.187 | 5.9988 | 5.8106 | 5.7595 | 5.7085 | 5.6574 | 5.6063 | 5.3574 | 5.3459 | 5.3344 | 5.3229 | 5.3115 | 5.3
RM3CoLosAngs | FlatDistPV | ATB_2019_mid | 17.9354 | 17.1023 | 16.992 | 16.009 | 15.7822 | 15.4175 | 15.0528 | 14.6881 | 14.3234 | 13.9588 | 13.5941 | 13.2294 | 12.8647 | 12.5 | 12.3824 | 12.2647 | 12.1471 | 12.0294 | 11.9118 | 11.7941 | 11.6765 | 11.5589 | 11.4412 | 11.3236 | 11.1912 | 11.0589 | 10.9265 | 10.7941 | 10.6618 | 10.5294 | 10.3971 | 10.2647 | 10.1324 | 10
RC3CoLosAngs | FlatDistPV | ATB_2019_high | 17.9354 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023 | 17.1023
RL3ReLosAngs | SlopedDistPV | ATB_2019_low | 23.4278 | 21.4755 | 18.7685 | 17.7363 | 16.6052 | 15.4742 | 14.3431 | 13.2121 | 12.0811 | 10.95 | 9.819 | 8.6879 | 7.5569 | 6.4259 | 6.2701 | 6.1143 | 5.9586 | 5.8028 | 5.6471 | 5.4913 | 5.3356 | 5.1798 | 5.024 | 4.8683 | 4.7938 | 4.7193 | 4.6448 | 4.5703 | 4.4958 | 4.4766 | 4.4575 | 4.4383 | 4.4192 | 4.4
RM3ReLosAngs | SlopedDistPV | ATB_2019_mid | 23.4278 | 21.4755 | 20.6026 | 20.0867 | 19.2049 | 18.323 | 17.4411 | 16.5592 | 15.6773 | 14.7955 | 13.9136 | 13.0317 | 12.1498 | 11.268 | 11.0539 | 10.8398 | 10.6258 | 10.4117 | 10.1977 | 9.9836 | 9.7696 | 9.5555 | 9.3415 | 9.1274 | 9.0356 | 8.9437 | 8.8518 | 8.76 | 8.6681 | 8.6465 | 8.6249 | 8.6033 | 8.5816 | 8.56
RC3ReLosAngs | SlopedDistPV | ATB_2019_high | 23.4278 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755 | 21.4755
RL3LaLTRG11 | OnshoreWind | ATB_2019_low | 43.56 | 42.8538 | 42.1477 | 41.4415 | 40.7354 | 40.0292 | 39.3231 | 38.6169 | 37.9108 | 37.2046 | 36.4985 | 35.7923 | 35.0862 | 34.38 | 33.8643 | 33.3486 | 32.8329 | 32.3172 | 31.8015 | 31.2858 | 30.7701 | 30.2544 | 29.7387 | 29.223 | 28.7073 | 28.1916 | 27.6759 | 27.1602 | 26.6445 | 26.1288 | 25.6131 | 25.0974 | 24.5817 | 24.066
RM3LaLTRG11 | OnshoreWind | ATB_2019_mid | 43.56 | 43.2054 | 42.8508 | 42.4962 | 42.1415 | 41.7869 | 41.4323 | 41.0777 | 40.7231 | 40.3685 | 40.0138 | 39.6592 | 39.3046 | 38.95 | 38.6579 | 38.3658 | 38.0736 | 37.7815 | 37.4894 | 37.1973 | 36.9051 | 36.613 | 36.3209 | 36.0288 | 35.7366 | 35.4445 | 35.1524 | 34.8603 | 34.5681 | 34.276 | 33.9839 | 33.6917 | 33.3996 | 33.1075
RC3LaLTRG11 | OnshoreWind | ATB_2019_high | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56 | 43.56
RL3OfOTRG66 | OffshoreWind | ATB_2019_low | 87.4043 | 67.9543 | 66.0406 | 64.1809 | 62.3735 | 60.617 | 58.91 | 57.251 | 55.6388 | 54.0719 | 52.5492 | 51.0694 | 49.6312 | 48.2335 | 46.8752 | 45.5552 | 44.2723 | 43.0256 | 41.8139 | 40.6364 | 39.492 | 38.3799 | 37.2991 | 36.2487 | 35.2279 | 34.2359 | 33.2718 | 32.3348 | 31.4242 | 30.5393 | 29.6793 | 28.8435 | 28.0312 | 27.2418
RM3OfOTRG66 | OffshoreWind | ATB_2019_mid | 87.4043 | 84.9429 | 82.5508 | 80.2261 | 77.9669 | 75.7712 | 73.6374 | 71.5637 | 69.5484 | 67.5899 | 65.6865 | 63.8367 | 62.039 | 60.2919 | 58.5941 | 56.944 | 55.3404 | 53.782 | 52.2674 | 50.7955 | 49.3651 | 47.9749 | 46.6239 | 45.3109 | 44.0349 | 42.7948 | 41.5897 | 40.4185 | 39.2803 | 38.1741 | 37.0991 | 36.0543 | 35.039 | 34.0523
RC3OfOTRG66 | OffshoreWind | ATB_2019_high | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043 | 87.4043
| Battery_Bulk | ATB_2019_low | 37.1094 | 37.1094 | 33.0774 | 29.0454 | 26.8274 | 24.6094 | 22.3914 | 20.1734 | 17.9554 | 16.7936 | 15.6317 | 14.4699 | 13.3081 | 12.1463 | 11.9086 | 11.671 | 11.4333 | 11.1957 | 10.9581 | 10.7204 | 10.4828 | 10.2451 | 10.0075 | 9.7698 | 9.5322 | 9.2945 | 9.0569 | 8.8193 | 8.5816 | 8.344 | 8.1063 | 7.8687 | 7.631 | 7.3934
| Battery_Bulk | ATB_2019_mid | 37.1094 | 37.1094 | 34.6055 | 32.1016 | 30.5191 | 28.9366 | 27.354 | 25.7715 | 24.189 | 23.4029 | 22.6168 | 21.8307 | 21.0446 | 20.2585 | 20.0053 | 19.752 | 19.4988 | 19.2456 | 18.9924 | 18.7391 | 18.4859 | 18.2327 | 17.9794 | 17.7262 | 17.473 | 17.2197 | 16.9665 | 16.7133 | 16.46 | 16.2068 | 15.9536 | 15.7003 | 15.4471 | 15.1939
| Battery_Bulk | ATB_2019_high | 37.1094 | 37.1094 | 37.1094 | 35.9649 | 35.6539 | 35.343 | 35.032 | 34.721 | 34.4101 | 34.0991 | 33.7882 | 33.4772 | 33.1662 | 32.8553 | 32.7543 | 32.6533 | 32.5523 | 32.4514 | 32.3504 | 32.2494 | 32.1484 | 32.0475 | 31.9465 | 31.8455 | 31.7445 | 31.6436 | 31.5426 | 31.4416 | 31.3406 | 31.2397 | 31.1387 | 31.0377 | 30.9367 | 30.8358
| Battery_Conting | ATB_2019_low | 37.1094 | 37.1094 | 33.0774 | 29.0454 | 26.8274 | 24.6094 | 22.3914 | 20.1734 | 17.9554 | 16.7936 | 15.6317 | 14.4699 | 13.3081 | 12.1463 | 11.9086 | 11.671 | 11.4333 | 11.1957 | 10.9581 | 10.7204 | 10.4828 | 10.2451 | 10.0075 | 9.7698 | 9.5322 | 9.2945 | 9.0569 | 8.8193 | 8.5816 | 8.344 | 8.1063 | 7.8687 | 7.631 | 7.3934
| Battery_Conting | ATB_2019_mid | 37.1094 | 37.1094 | 34.6055 | 32.1016 | 30.5191 | 28.9366 | 27.354 | 25.7715 | 24.189 | 23.4029 | 22.6168 | 21.8307 | 21.0446 | 20.2585 | 20.0053 | 19.752 | 19.4988 | 19.2456 | 18.9924 | 18.7391 | 18.4859 | 18.2327 | 17.9794 | 17.7262 | 17.473 | 17.2197 | 16.9665 | 16.7133 | 16.46 | 16.2068 | 15.9536 | 15.7003 | 15.4471 | 15.1939
| Battery_Conting | ATB_2019_high | 37.1094 | 37.1094 | 37.1094 | 35.9649 | 35.6539 | 35.343 | 35.032 | 34.721 | 34.4101 | 34.0991 | 33.7882 | 33.4772 | 33.1662 | 32.8553 | 32.7543 | 32.6533 | 32.5523 | 32.4514 | 32.3504 | 32.2494 | 32.1484 | 32.0475 | 31.9465 | 31.8455 | 31.7445 | 31.6436 | 31.5426 | 31.4416 | 31.3406 | 31.2397 | 31.1387 | 31.0377 | 30.9367 | 30.8358
| Battery_Reg | ATB_2019_low | 37.1094 | 37.1094 | 33.0774 | 29.0454 | 26.8274 | 24.6094 | 22.3914 | 20.1734 | 17.9554 | 16.7936 | 15.6317 | 14.4699 | 13.3081 | 12.1463 | 11.9086 | 11.671 | 11.4333 | 11.1957 | 10.9581 | 10.7204 | 10.4828 | 10.2451 | 10.0075 | 9.7698 | 9.5322 | 9.2945 | 9.0569 | 8.8193 | 8.5816 | 8.344 | 8.1063 | 7.8687 | 7.631 | 7.3934
| Battery_Reg | ATB_2019_mid | 37.1094 | 37.1094 | 34.6055 | 32.1016 | 30.5191 | 28.9366 | 27.354 | 25.7715 | 24.189 | 23.4029 | 22.6168 | 21.8307 | 21.0446 | 20.2585 | 20.0053 | 19.752 | 19.4988 | 19.2456 | 18.9924 | 18.7391 | 18.4859 | 18.2327 | 17.9794 | 17.7262 | 17.473 | 17.2197 | 16.9665 | 16.7133 | 16.46 | 16.2068 | 15.9536 | 15.7003 | 15.4471 | 15.1939
| Battery_Reg | ATB_2019_high | 37.1094 | 37.1094 | 37.1094 | 35.9649 | 35.6539 | 35.343 | 35.032 | 34.721 | 34.4101 | 34.0991 | 33.7882 | 33.4772 | 33.1662 | 32.8553 | 32.7543 | 32.6533 | 32.5523 | 32.4514 | 32.3504 | 32.2494 | 32.1484 | 32.0475 | 31.9465 | 31.8455 | 31.7445 | 31.6436 | 31.5426 | 31.4416 | 31.3406 | 31.2397 | 31.1387 | 31.0377 | 30.9367 | 30.8358
| Variable O&M ($/MWh) | NOTE: ATB 2019 summary sheet combines fixed and variable O&M into a single number; we use that number for fixed O&M and zero out variable O&M, since that is always zero; double-check in future years
| Technology | Scenario | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
RL3UtLosAngs | CentralTrackingPV | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RM3UtLosAngs | CentralTrackingPV | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RC3UtLosAngs | CentralTrackingPV | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RL3CoLosAngs | FlatDistPV | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RM3CoLosAngs | FlatDistPV | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RC3CoLosAngs | FlatDistPV | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RL3ReLosAngs | SlopedDistPV | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RM3ReLosAngs | SlopedDistPV | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RC3ReLosAngs | SlopedDistPV | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RL3LaLTRG11 | OnshoreWind | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RM3LaLTRG11 | OnshoreWind | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RC3LaLTRG11 | OnshoreWind | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RL3OfOTRG66 | OffshoreWind | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RM3OfOTRG66 | OffshoreWind | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RC3OfOTRG66 | OffshoreWind | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Bulk | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Bulk | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Bulk | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Conting | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Conting | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Conting | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| regional capital cost ($/kW) |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| CentralTrackingPV | ATB_2019_low | 1821.5975 | 1828.1984 | 1577.0319 | 1479.6514 | 1424.2912 | 1368.931 | 1313.5709 | 1258.2107 | 1202.8505 | 1147.4903 | 1092.1301 | 1036.7699 | 981.4098 | 926.0496 | 899.5641 | 873.0786 | 846.5931 | 820.1076 | 793.6221 | 773.5255 | 753.4289 | 733.3324 | 713.2358 | 693.1392 | 680.9496 | 668.7599 | 656.5702 | 644.3806 | 632.1909 | 622.5102 | 612.8296 | 603.1489 | 593.4682 | 583.7875
| CentralTrackingPV | ATB_2019_mid | 1821.5975 | 1828.1984 | 1796.0236 | 1762.2555 | 1729.0054 | 1693.9081 | 1658.8108 | 1623.7134 | 1588.6161 | 1553.5188 | 1518.4214 | 1483.3241 | 1448.2268 | 1413.1294 | 1397.4628 | 1381.7961 | 1366.1294 | 1350.4627 | 1334.796 | 1319.1294 | 1303.4627 | 1287.796 | 1272.1293 | 1256.4626 | 1242.8793 | 1229.2959 | 1215.7125 | 1202.1291 | 1188.5457 | 1174.9624 | 1161.379 | 1147.7956 | 1134.2122 | 1120.6288
| CentralTrackingPV | ATB_2019_high | 1821.5975 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984 | 1828.1984
| FlatDistPV | ATB_2019_low | 3008.3404 | 2932.2223 | 2158.9664 | 2021.6089 | 1818.9533 | 1757.2194 | 1695.4856 | 1633.7518 | 1572.018 | 1510.2842 | 1448.5504 | 1386.8165 | 1325.0827 | 1263.3489 | 1232.437 | 1201.525 | 1170.6131 | 1139.7011 | 1108.7892 | 1077.8772 | 1046.9653 | 1016.0534 | 985.1414 | 954.2295 | 945.8448 | 937.46 | 929.0753 | 920.6906 | 879.8006 | 877.9169 | 876.0333 | 874.1496 | 872.266 | 870.3823
| FlatDistPV | ATB_2019_mid | 3008.3404 | 2932.2223 | 2790.472 | 2629.0446 | 2591.8013 | 2531.911 | 2472.0206 | 2412.1303 | 2352.24 | 2292.3497 | 2232.4594 | 2172.5691 | 2112.6788 | 2052.7885 | 2033.4688 | 2014.1491 | 1994.8294 | 1975.5097 | 1956.19 | 1936.8703 | 1917.5506 | 1898.2309 | 1878.9112 | 1859.5915 | 1837.8554 | 1816.1194 | 1794.3833 | 1772.6472 | 1750.9111 | 1729.1751 | 1707.439 | 1685.7029 | 1663.9668 | 1642.2308
| FlatDistPV | ATB_2019_high | 3008.3404 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223 | 2932.2223
| SlopedDistPV | ATB_2019_low | 4486.9711 | 4276.4717 | 3800.6269 | 3591.5924 | 3362.5567 | 3133.521 | 2904.4854 | 2675.4497 | 2446.414 | 2217.3783 | 1988.3427 | 1759.307 | 1530.2713 | 1301.2356 | 1269.6949 | 1238.1541 | 1206.6134 | 1175.0727 | 1143.532 | 1111.9912 | 1080.4505 | 1048.9098 | 1017.369 | 985.8283 | 970.7421 | 955.656 | 940.5698 | 925.4837 | 910.3975 | 906.518 | 902.6385 | 898.759 | 894.8795 | 891
| SlopedDistPV | ATB_2019_mid | 4486.9711 | 4276.4717 | 4172.0188 | 4067.5659 | 3888.9854 | 3710.4048 | 3531.8243 | 3353.2437 | 3174.6632 | 2996.0827 | 2817.5021 | 2638.9216 | 2460.341 | 2281.7605 | 2238.4144 | 2195.0683 | 2151.7222 | 2108.3761 | 2065.03 | 2021.6839 | 1978.3378 | 1934.9917 | 1891.6456 | 1848.2995 | 1829.6989 | 1811.0983 | 1792.4977 | 1773.8971 | 1755.2965 | 1750.9172 | 1746.5379 | 1742.1586 | 1737.7793 | 1733.4
| SlopedDistPV | ATB_2019_high | 4486.9711 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717 | 4276.4717
| OnshoreWind | ATB_2019_low | 2173.6466 | 2123.2201 | 2072.7937 | 2022.3672 | 1971.9407 | 1921.5142 | 1871.0877 | 1820.6613 | 1770.2348 | 1719.8083 | 1669.3818 | 1618.9554 | 1568.5289 | 1518.1024 | 1497.8189 | 1477.4596 | 1457.0245 | 1436.5137 | 1415.927 | 1395.2646 | 1374.5265 | 1353.7125 | 1332.8228 | 1311.8573 | 1290.816 | 1269.6989 | 1248.5061 | 1227.2374 | 1205.893 | 1184.4729 | 1162.9769 | 1141.4052 | 1119.7577 | 1098.0344
| OnshoreWind | ATB_2019_mid | 2173.6466 | 2136.4903 | 2099.3339 | 2062.1776 | 2025.0212 | 1987.8648 | 1950.7085 | 1913.5521 | 1876.3958 | 1839.2394 | 1802.0831 | 1764.9267 | 1727.7704 | 1690.614 | 1672.3534 | 1654.0649 | 1635.7486 | 1617.4045 | 1599.0325 | 1580.6327 | 1562.2051 | 1543.7496 | 1525.2663 | 1506.7552 | 1488.2162 | 1469.6494 | 1451.0547 | 1432.4322 | 1413.7819 | 1395.1038 | 1376.3978 | 1357.6639 | 1338.9023 | 1320.1128
| OnshoreWind | ATB_2019_high | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466 | 2173.6466
| OffshoreWind | ATB_2019_low | 7468.2398 | 5759.9917 | 5554.0718 | 5356.4732 | 5166.8519 | 4984.8782 | 4810.2358 | 4642.6219 | 4481.7461 | 4327.33 | 4179.1069 | 4036.8211 | 3900.2274 | 3769.0909 | 3643.1864 | 3522.2982 | 3406.2193 | 3294.7514 | 3187.7044 | 3084.8962 | 2986.1521 | 2891.3048 | 2800.1938 | 2712.6653 | 2628.572 | 2547.7724 | 2470.1313 | 2395.5187 | 2323.8102 | 2254.8866 | 2188.6335 | 2124.9413 | 2063.705 | 2004.824
| OffshoreWind | ATB_2019_mid | 7468.2398 | 7199.9896 | 6942.5897 | 6695.5915 | 6458.5649 | 6231.0977 | 6012.7947 | 5803.2774 | 5602.1826 | 5409.1625 | 5223.8837 | 5046.0263 | 4875.2842 | 4711.3636 | 4553.983 | 4402.8727 | 4257.7741 | 4118.4392 | 3984.6305 | 3856.1203 | 3732.6902 | 3614.131 | 3500.2423 | 3390.8317 | 3285.715 | 3184.7155 | 3087.6641 | 2994.3983 | 2904.7627 | 2818.6082 | 2735.7919 | 2656.1767 | 2579.6313 | 2506.03
| OffshoreWind | ATB_2019_high | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398 | 7468.2398
| Battery_Bulk | ATB_2019_low | 855 | 855 | 762.1036 | 669.2071 | 618.104 | 567.0009 | 515.8979 | 464.7948 | 413.6917 | 386.9234 | 360.1551 | 333.3868 | 306.6185 | 279.8503 | 274.3749 | 268.8996 | 263.4243 | 257.9489 | 252.4736 | 246.9983 | 241.5229 | 236.0476 | 230.5723 | 225.0969 | 219.6216 | 214.1463 | 208.6709 | 203.1956 | 197.7203 | 192.245 | 186.7696 | 181.2943 | 175.819 | 170.3436
| Battery_Bulk | ATB_2019_mid | 855 | 855 | 797.3107 | 739.6214 | 703.1599 | 666.6984 | 630.2368 | 593.7753 | 557.3138 | 539.2022 | 521.0907 | 502.9792 | 484.8676 | 466.7561 | 460.9216 | 455.0872 | 449.2527 | 443.4183 | 437.5838 | 431.7494 | 425.9149 | 420.0805 | 414.246 | 408.4116 | 402.5771 | 396.7427 | 390.9082 | 385.0738 | 379.2393 | 373.4049 | 367.5704 | 361.736 | 355.9015 | 350.0671
| Battery_Bulk | ATB_2019_high | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
| Battery_Conting | ATB_2019_low | 985.625 | 985.625 | 878.5361 | 771.4471 | 712.5366 | 653.6261 | 594.7156 | 535.8051 | 476.8946 | 446.0367 | 415.1788 | 384.3209 | 353.463 | 322.6052 | 316.2933 | 309.9815 | 303.6696 | 297.3578 | 291.046 | 284.7341 | 278.4223 | 272.1104 | 265.7986 | 259.4868 | 253.1749 | 246.8631 | 240.5512 | 234.2394 | 227.9276 | 221.6157 | 215.3039 | 208.992 | 202.6802 | 196.3684
| Battery_Conting | ATB_2019_mid | 985.625 | 985.625 | 919.1221 | 852.6191 | 810.5871 | 768.555 | 726.523 | 684.491 | 642.4589 | 621.5804 | 600.7018 | 579.8232 | 558.9446 | 538.0661 | 531.3402 | 524.6144 | 517.8886 | 511.1627 | 504.4369 | 497.7111 | 490.9853 | 484.2594 | 477.5336 | 470.8078 | 464.082 | 457.3561 | 450.6303 | 443.9045 | 437.1787 | 430.4528 | 423.727 | 417.0012 | 410.2754 | 403.5495
| Battery_Conting | ATB_2019_high | 985.625 | 985.625 | 985.625 | 978.3002 | 976.3101 | 974.3199 | 972.3298 | 970.3396 | 968.3495 | 966.3593 | 964.3692 | 962.379 | 960.3889 | 958.3987 | 957.7525 | 957.1062 | 956.46 | 955.8137 | 955.1675 | 954.5213 | 953.875 | 953.2288 | 952.5825 | 951.9363 | 951.2901 | 950.6438 | 949.9976 | 949.3513 | 948.7051 | 948.0588 | 947.4126 | 946.7664 | 946.1201 | 945.4739
| Battery_Reg | ATB_2019_low | 1116.25 | 1116.25 | 994.9685 | 873.6871 | 806.9692 | 740.2512 | 673.5333 | 606.8154 | 540.0975 | 505.15 | 470.2025 | 435.255 | 400.3075 | 365.3601 | 358.2117 | 351.0634 | 343.915 | 336.7667 | 329.6183 | 322.47 | 315.3216 | 308.1733 | 301.0249 | 293.8766 | 286.7282 | 279.5799 | 272.4315 | 265.2832 | 258.1348 | 250.9865 | 243.8381 | 236.6898 | 229.5414 | 222.3931
| Battery_Reg | ATB_2019_mid | 1116.25 | 1116.25 | 1040.9334 | 965.6168 | 918.0143 | 870.4117 | 822.8092 | 775.2066 | 727.6041 | 703.9585 | 680.3129 | 656.6672 | 633.0216 | 609.376 | 601.7588 | 594.1416 | 586.5244 | 578.9072 | 571.29 | 563.6728 | 556.0556 | 548.4384 | 540.8212 | 533.204 | 525.5868 | 517.9696 | 510.3524 | 502.7352 | 495.118 | 487.5008 | 479.8836 | 472.2664 | 464.6492 | 457.032
| Battery_Reg | ATB_2019_high | 1116.25 | 1116.25 | 1116.25 | 1101.6005 | 1097.6202 | 1093.6399 | 1089.6596 | 1085.6792 | 1081.6989 | 1077.7186 | 1073.7383 | 1069.758 | 1065.7777 | 1061.7974 | 1060.5049 | 1059.2125 | 1057.92 | 1056.6275 | 1055.335 | 1054.0425 | 1052.75 | 1051.4576 | 1050.1651 | 1048.8726 | 1047.5801 | 1046.2876 | 1044.9951 | 1043.7026 | 1042.4102 | 1041.1177 | 1039.8252 | 1038.5327 | 1037.2402 | 1035.9477
| regional energy capital cost ($/kWh) |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Battery_Bulk | ATB_2019_low | 261.25 | 261.25 | 232.865 | 204.48 | 188.8651 | 173.2503 | 157.6355 | 142.0206 | 126.4058 | 118.2266 | 110.0474 | 101.8682 | 93.689 | 85.5098 | 83.8368 | 82.1638 | 80.4907 | 78.8177 | 77.1447 | 75.4717 | 73.7987 | 72.1257 | 70.4526 | 68.7796 | 67.1066 | 65.4336 | 63.7606 | 62.0876 | 60.4145 | 58.7415 | 57.0685 | 55.3955 | 53.7225 | 52.0494
| Battery_Bulk | ATB_2019_mid | 261.25 | 261.25 | 243.6227 | 225.9954 | 214.8544 | 203.7134 | 192.5724 | 181.4313 | 170.2903 | 164.7562 | 159.2222 | 153.6881 | 148.154 | 142.6199 | 140.8372 | 139.0544 | 137.2717 | 135.4889 | 133.7062 | 131.9234 | 130.1407 | 128.3579 | 126.5752 | 124.7924 | 123.0097 | 121.2269 | 119.4442 | 117.6614 | 115.8787 | 114.0959 | 112.3132 | 110.5304 | 108.7477 | 106.9649
| Battery_Bulk | ATB_2019_high | 261.25 | 261.25 | 261.25 | 246.6005 | 242.6202 | 238.6399 | 234.6596 | 230.6792 | 226.6989 | 222.7186 | 218.7383 | 214.758 | 210.7777 | 206.7974 | 205.5049 | 204.2125 | 202.92 | 201.6275 | 200.335 | 199.0425 | 197.75 | 196.4576 | 195.1651 | 193.8726 | 192.5801 | 191.2876 | 189.9951 | 188.7026 | 187.4102 | 186.1177 | 184.8252 | 183.5327 | 182.2402 | 180.9477
| Battery_Conting | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Conting | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Conting | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_mid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Battery_Reg | ATB_2019_high | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M lookup | 2020-2050 average
| CentralTrackingPVATB_2019_low | 0
| CentralTrackingPVATB_2019_mid | 0
| CentralTrackingPVATB_2019_high | 0
| FlatDistPVATB_2019_low | 0
| FlatDistPVATB_2019_mid | 0
| FlatDistPVATB_2019_high | 0
| SlopedDistPVATB_2019_low | 0
| SlopedDistPVATB_2019_mid | 0
| SlopedDistPVATB_2019_high | 0
| OnshoreWindATB_2019_low | 0
| OnshoreWindATB_2019_mid | 0
| OnshoreWindATB_2019_high | 0
| OffshoreWindATB_2019_low | 0
| OffshoreWindATB_2019_mid | 0
| OffshoreWindATB_2019_high | 0
| Battery_BulkATB_2019_low | 0
| Battery_BulkATB_2019_mid | 0
| Battery_BulkATB_2019_high | 0
| Battery_ContingATB_2019_low | 0
| Battery_ContingATB_2019_mid | 0
| Battery_ContingATB_2019_high | 0
| Battery_RegATB_2019_low | 0
| Battery_RegATB_2019_mid | 0
| Battery_RegATB_2019_high | 0
Note on B6: From each technology page in NREL ATB 2019 https://atb.nrel.gov/electricity/2019/
Note on B7: From https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capcost_assumption.pdf as recommended by https://atb.nrel.gov/electricity/2019/regional-capex.html. Similar values are also in https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/beret_addendum_leidos.pdf
Note on C7: for 150 MW facility (20 MW is 63%)
Note on D7: assumed same as 20MW fixed-tilt project
Note on E7: assumed same as 20MW fixed-tilt project
Note on H7: for 8-hour system shown in https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/beret_addendum_leidos.pdf instead of 2-hour system in https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capcost_assumption.pdf (which is 32%)
Note on B8: From pp. 22, 28 and 38 of https://www.nrel.gov/docs/fy19osti/72399.pdf and https://atb.nrel.gov/electricity/2019/index.html?t=su
Note on B9: From pp. 22, 28 and 38 of https://www.nrel.gov/docs/fy19osti/72399.pdf
Note on B10: From pp. 17, 25 and 31 of https://www.nrel.gov/docs/fy19osti/72399.pdf
Note on B11: From pp. 22, 28 and 38 of https://www.nrel.gov/docs/fy19osti/72399.pdf
Note on C12: From NREL ATB https://atb.nrel.gov/electricity/2019/index.html?t=su
Note on D12: From NREL ATB https://atb.nrel.gov/electricity/2019/index.html?t=su
Note on E12: From NREL ATB https://atb.nrel.gov/electricity/2019/index.html?t=su
Note on B13: formula for sum of geometric progression from https://math.stackexchange.com/a/1897065/425405
Note on H15: From specifications for reference storage system in ATB workbook, https://data.nrel.gov/files/89/2018-ATB-data-interim-geo.xlsm, originally from cole_utility-scale_2016 http://dx.doi.org/10.1109/NAPS.2016.7747866
Note on B24: Based on commercial distributed PV in ATB
Note on B27: based on residential PV in ATB
Note on B30: We assume all Oahu wind has costs corresponding to class TRG6 in ATB (6.1-9.4 m/s annual speeds), since 82% of our turbines are between 6 and 7.5 m/s and 13% are between 7.5 and 8.5 m/s (see psql turbines table). TODO: cluster into wind farms, assign same turbine model to each farm, divide projects into different technologies for different years, with improving capacity factors, as described in ATB (with either-or selection for projects on same site).
Note on B33: Used costs for ATB TRG7, floating wind 40 km offshore, because Oahu projects are 20-25 miles (32-40 km) offshore.
Note on B39: Modeled as zero bulk energy storage, with same cost as 0.5 hours of storage, per PSIP
Note on B42: Modeled as zero bulk energy storage, but with cost equivalent to 1 hour of energy storage, per PSIP
Note on B51: Modeled as zero bulk energy storage, with same cost as 0.5 hours of storage, per PSIP
Note on B54: Modeled as zero bulk energy storage, but with cost equivalent to 1 hour of energy storage, per PSIP TODO: figure out duty cycle for regulating batteries, and use that to calculate variable cost of providing regulating reserves (and move that into Switch) and to make sure these will stay within cycle life with only 1 hour of capacity Notes: * http://batteryuniversity.com/learn/article/how_to_prolong_lithium_based_batteries shows that shallower cycles and staying in middle of SOC range sharply extend the total amount of kWh that can be cycled through the battery; this is exactly the duty cycle that would be used for regulation. Also, the HECO storage page indicates that 15,000 cycles/year are possible for regulation, assuming 20% maximum depth of discharge and 1 hour of storage capacity (probably real duty cycle is assumed to be much less than 20% discharge, but it also may not matter how big the average swings are, because they always stay near the middle of the SOC/voltage level). * Tesla warranty indicates cycling equal to 2800x energy content is possible (37.8 MWh for 13.5 kW PowerWall 2 battery, https://www.tesla.com/sites/default/files/pdfs/powerwall/powerwall_2_ac_warranty_us_1-4.pdf) (could just assume double this is possibble with shallow cycles, based on the batteryuniversity graphs) * PJM RTO regulation signal (http://www.pjm.com/markets-and-operations/ancillary-services/) cited in SAND2016- 4502J (https://www.osti.gov/pages/servlets/purl/1257783) has average charging/discharging load of about 28%, which would be equivalent to 2452 hours of charging a year, which doesn't seem like it could be met by 1 hour of capacity with a limit around 365 cycles/year. But this may be for intensively used regulating resources (as procured in small amounts in current PJM markets), rather than the lightly-used reserves that would be needed for backing up wind and solar at the rate that we do in Switch-Hawaii. * TODO: Look at the average amount of charging and/or discharging per hour for batteries used to provide Hawaii-scale reserves for wind or solar on Oahu -- use HSIS one-minute solar data and midwest or ERCOT one-minute wind data.